## 25F nomo
Chief Joseph-Monroe #1 500kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 011R1
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6546.7433
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 109.45 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 825.03 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 469.61 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 994.89 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 825.03 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1266.17 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 271.23 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1753.44 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 640.91 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2050.91 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 994.89 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 469.61 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 548.25 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 640.91 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 916.76 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 916.76 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1266.17 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1401.9 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1035.58 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1815.44 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 1401.9 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 109.45 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1753.44 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 271.23 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1452.6 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 548.25 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1815.44 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1035.58 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 2050.91 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1452.6 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Chief Joseph-Monroe #1 500kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 011R1
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6408.6087
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 159.99 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 879.97 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 528.15 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1050.27 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 879.97 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1319.56 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 9.74 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1690.99 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 695.41 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1735.65 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1050.27 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 528.15 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 293.01 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 695.41 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 972.28 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 972.28 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1319.56 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1460.71 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 756.47 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1522.55 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 1460.71 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 159.99 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1690.99 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 9.74 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1189.47 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 293.01 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1522.55 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 756.47 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1735.65 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1189.47 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Chief Joseph-Monroe #1 500kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 011R1
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 5965.134
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -10.52 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 965.88 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 306.66 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 814.81 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 965.88 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1052.76 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 168.29 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1420.54 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 501.46 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1729.56 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 814.81 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 306.66 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 440.15 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 501.46 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 775.56 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 775.56 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1052.76 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1238.59 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 906.79 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1685.4 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 1238.59 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -10.52 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1420.54 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 168.29 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1318.88 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 440.15 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1685.4 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 906.79 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1729.56 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1318.88 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Chief Joseph-Monroe #1 500kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 011R1
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4917.2667
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 498.79 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 701.31 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 722.25 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 832.55 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 701.31 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1049.08 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 683.27 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1443.25 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 871.31 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1501.52 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 832.55 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 722.25 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 960.32 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 871.31 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 1099.52 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1099.52 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1049.08 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1456.41 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1507.2 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1570.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1456.41 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 498.79 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1443.25 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 683.27 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1644.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 960.32 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1570.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1507.2 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1501.52 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1644.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Chief Joseph-Monroe #1 500kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 011R1
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4591.968
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 776.59 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 692.52 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 741.62 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 819.49 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 692.52 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1036.37 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 898.74 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1440.52 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 866.11 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1292.46 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 819.49 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 741.62 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 1098.94 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 866.11 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 1076.04 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1076.04 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1036.37 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1490.38 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1478.61 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1378.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1490.38 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 776.59 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1440.52 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 898.74 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1469.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1098.94 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1378.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1478.61 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1292.46 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1469.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Chief Joseph-Monroe #1 500kV Line(COV-CRES BYP @ COV)
G0 | 109.45 | 159.99 | -10.52 | 498.79 | 776.59
G1 | 469.61 | 528.15 | 306.66 | 722.25 | 741.62 | Season/Year: | WINTER 2009
G2 | 825.03 | 879.97 | 965.88 | 701.31 | 692.52 | Direction: | South-to-North (SN)
G3 | 271.23 | 9.74 | 168.29 | 683.27 | 898.74 | Case Loads: | Heavy Loads
G4 | 640.91 | 695.41 | 501.46 | 871.31 | 866.11 | Outage: | 011R1
G5 | 994.89 | 1050.27 | 814.81 | 832.55 | 819.49 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 548.25 | 293.01 | 440.15 | 960.32 | 1098.94 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 916.76 | 972.28 | 775.56 | 1099.52 | 1076.04 | Study Person: | FRP9899
G8 | 1266.17 | 1319.56 | 1052.76 | 1049.08 | 1036.37 | Source: | 011R1WINTER09v5SNH
G9 | 1035.58 | 756.47 | 906.79 | 1507.2 | 1478.61
G10 | 1401.9 | 1460.71 | 1238.59 | 1456.41 | 1490.38
G11 | 1753.44 | 1690.99 | 1420.54 | 1443.25 | 1440.52
G12 | 1452.6 | 1189.47 | 1318.88 | 1644.16 | 1469.12
G13 | 1815.44 | 1522.55 | 1685.4 | 1570.61 | 1378.55
G14 | 2050.91 | 1735.65 | 1729.56 | 1501.52 | 1292.46
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 011R1 | Chief Joseph-Monroe #1 500kV Line(COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6546.7433 | 109.45 | 469.61 | 825.03 | 271.23 | 640.91 | 994.89 | 548.25 | 916.76 | 1266.17 | 1035.58 | 1401.9 | 1753.44 | 1452.6 | 1815.44 | 2050.91
35F | 6408.6087 | 159.99 | 528.15 | 879.97 | 9.74 | 695.41 | 1050.27 | 293.01 | 972.28 | 1319.56 | 756.47 | 1460.71 | 1690.99 | 1189.47 | 1522.55 | 1735.65
45F | 5965.134 | -10.52 | 306.66 | 965.88 | 168.29 | 501.46 | 814.81 | 440.15 | 775.56 | 1052.76 | 906.79 | 1238.59 | 1420.54 | 1318.88 | 1685.4 | 1729.56
60F | 4917.2667 | 498.79 | 722.25 | 701.31 | 683.27 | 871.31 | 832.55 | 960.32 | 1099.52 | 1049.08 | 1507.2 | 1456.41 | 1443.25 | 1644.16 | 1570.61 | 1501.52
70F | 4591.968 | 776.59 | 741.62 | 692.52 | 898.74 | 866.11 | 819.49 | 1098.94 | 1076.04 | 1036.37 | 1478.61 | 1490.38 | 1440.52 | 1469.12 | 1378.55 | 1292.46

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 109.12 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 15.76 | 536.73 | 536.75 | 6580.16 | 109.45 | -1378.53 | CTG_FAIL_IN_FULL
G1 | 471.59 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 15.76 | 536.38 | 536.37 | 6517.52 | 469.61 | -1582.3 | CTG_FAIL_IN_FULL
G2 | 827.44 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 15.76 | 537.32 | 537.01 | 6537.5 | 825.03 | -1769.92 | CTG_FAIL_IN_FULL
G3 | 271.87 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 15.76 | 535.96 | 535.52 | 6578.2 | 271.23 | -1418.15 | CTG_FAIL_IN_FULL
G4 | 640.45 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 15.76 | 536.26 | 535.82 | 6515.96 | 640.91 | -1619.54 | CTG_FAIL_IN_FULL
G5 | 994.72 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 15.76 | 536.69 | 536.69 | 6537.23 | 994.89 | -1814.86 | CTG_FAIL_IN_FULL
G6 | 547.79 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 15.76 | 535.55 | 535.26 | 6577.77 | 548.25 | -1462.15 | CTG_FAIL_IN_FULL
G7 | 918.56 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 15.76 | 536.11 | 535.86 | 6516.03 | 916.76 | -1662.81 | CTG_FAIL_IN_FULL
G8 | 1266.92 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 15.76 | 536.85 | 536.81 | 6537.4 | 1266.17 | -1854.88 | CTG_FAIL_IN_FULL
G9 | 1037.35 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 15.76 | 535.71 | 535.48 | 6583.06 | 1035.58 | -1542.88 | CTG_FAIL_IN_FULL
G10 | 1401.08 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 15.76 | 535.74 | 535.64 | 6520.15 | 1401.9 | -1743.67 | CTG_FAIL_IN_FULL
G11 | 1752.97 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 15.76 | 536.9 | 536.89 | 6542.38 | 1753.44 | -1935.24 | CTG_FAIL_IN_FULL
G12 | 1452.61 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 15.76 | 535.85 | 535.83 | 6588.21 | 1452.6 | -1636.69 | CTG_FAIL_IN_FULL
G13 | 1815.59 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 15.76 | 535.96 | 535.96 | 6526.19 | 1815.44 | -1836.37 | CTG_FAIL_IN_FULL
G14 | 2051.09 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -19.82 | -508.06 | -508.03 | 6543.39 | 2050.91 | -1944.51 | CTG_FAIL_IN_FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 161.65 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 15.76 | 518.5 | 518.22 | 6443.54 | 159.99 | -1378.82 | CTG_FAIL_IN_FULL
G1 | 527.73 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 15.76 | 519.19 | 518.93 | 6381.71 | 528.15 | -1580.5 | CTG_FAIL_IN_FULL
G2 | 882.13 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 15.76 | 519.68 | 519.39 | 6402.17 | 879.97 | -1772.41 | CTG_FAIL_IN_FULL
G3 | 9.13 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 17.3 | 486.31 | 486.5 | 6435.37 | 9.74 | -1185.64 | FULL
G4 | 696.87 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 15.76 | 518.91 | 518.68 | 6380.55 | 695.41 | -1615.2 | CTG_FAIL_IN_FULL
G5 | 1052.33 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 15.76 | 519.59 | 519.33 | 6401.94 | 1050.27 | -1810.06 | CTG_FAIL_IN_FULL
G6 | 292.56 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 17.3 | 487.15 | 486.93 | 6435.65 | 293.01 | -1230.88 | FULL
G7 | 974.15 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 15.76 | 518.79 | 518.53 | 6380.77 | 972.28 | -1658.22 | CTG_FAIL_IN_FULL
G8 | 1319.55 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -19.82 | -491.86 | -491.86 | 6401.49 | 1319.56 | -1847.51 | CTG_FAIL_IN_FULL
G9 | 756.45 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 17.3 | 471.18 | 471.63 | 6442.28 | 756.47 | -1296.37 | FULL
G10 | 1459.96 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 15.76 | 518.66 | 518.57 | 6386 | 1460.71 | -1740.24 | CTG_FAIL_IN_FULL
G11 | 1690.85 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -19.82 | -492.49 | -492.48 | 6402.8 | 1690.99 | -1845.62 | CTG_FAIL_IN_FULL
G12 | 1189.27 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 17.3 | 487.31 | 487.65 | 6448.26 | 1189.47 | -1402.8 | FULL
G13 | 1522.82 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 17.3 | 484.8 | 485.21 | 6386.04 | 1522.55 | -1580.93 | FULL
G14 | 1736.06 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -21.82 | -426.25 | -426.31 | 6400.56 | 1735.65 | -1671.97 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -11.24 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 17.4 | 474.52 | 474.01 | 5996.88 | -10.52 | -1182.36 | FULL
G1 | 306.1 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 17.3 | 458.33 | 458.54 | 5933.25 | 306.66 | -1350.53 | FULL
G2 | 967.15 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -19.82 | -477.7 | -477.27 | 5961.29 | 965.88 | -1767.34 | CTG_FAIL_IN_FULL
G3 | 166.79 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 17.4 | 475.87 | 475.6 | 5996.9 | 168.29 | -1225.74 | FULL
G4 | 501.11 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 17.3 | 474.6 | 474.77 | 5933.2 | 501.46 | -1404.55 | FULL
G5 | 814.39 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -21.82 | -408.01 | -408.62 | 5952.2 | 814.81 | -1571.58 | FULL
G6 | 441.35 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 17.4 | 475.46 | 475.93 | 5997.25 | 440.15 | -1266.1 | FULL
G7 | 777.16 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 17.3 | 475.04 | 475.03 | 5933.95 | 775.56 | -1447.65 | FULL
G8 | 1053.91 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -21.82 | -412.81 | -412.98 | 5951.56 | 1052.76 | -1588.77 | FULL
G9 | 908.67 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 17.4 | 476.3 | 476.47 | 6003.78 | 906.79 | -1339.38 | FULL
G10 | 1238.87 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 17.3 | 459.51 | 460.01 | 5941.47 | 1238.59 | -1515.09 | FULL
G11 | 1420.54 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -415.22 | -415.28 | 5955.25 | 1420.54 | -1575.76 | FULL
G12 | 1319.13 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 17.4 | 476.19 | 476.36 | 6011.09 | 1318.88 | -1431.37 | FULL
G13 | 1685.69 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -21.82 | -393.88 | -393.53 | 5949.56 | 1685.4 | -1632.45 | FULL
G14 | 1729.67 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -422.48 | -422.35 | 5959.38 | 1729.56 | -1593.62 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 498.38 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 17.3 | 432.41 | 432.06 | 4954.52 | 498.79 | -1326.39 | FULL
G1 | 720.17 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -395.26 | -395.16 | 4888.71 | 722.25 | -1426.75 | FULL
G2 | 701 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -405.85 | -405.83 | 4899.06 | 701.31 | -1360.36 | FULL
G3 | 682.99 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 17.3 | 434.85 | 434.56 | 4955.26 | 683.27 | -1373.89 | FULL
G4 | 872.44 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -402.17 | -402.1 | 4889.63 | 871.31 | -1448.16 | FULL
G5 | 832.18 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -408.84 | -408.83 | 4898.84 | 832.55 | -1358.23 | FULL
G6 | 960.13 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 17.3 | 435.57 | 435.36 | 4957.66 | 960.32 | -1421.95 | FULL
G7 | 1098.22 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -404.41 | -404.4 | 4888.56 | 1099.52 | -1468.34 | FULL
G8 | 1050.98 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -410.69 | -411.09 | 4898.23 | 1049.08 | -1359.64 | FULL
G9 | 1508.26 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -398.01 | -397.97 | 4966.08 | 1507.2 | -1558.93 | FULL
G10 | 1456.5 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -403.78 | -404.29 | 4893.59 | 1456.41 | -1456.32 | FULL
G11 | 1443.1 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -415 | -414.74 | 4903.92 | 1443.25 | -1376.52 | FULL
G12 | 1645.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.02 | -419.81 | -419.76 | 4966.24 | 1644.16 | -1446.78 | FULL
G13 | 1573.02 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.02 | -421.49 | -421.45 | 4894.3 | 1570.61 | -1332.22 | FULL
G14 | 1499.49 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.02 | -422.98 | -422.94 | 4904.4 | 1501.52 | -1220.12 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 775.62 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -387.38 | -387.31 | 4635.15 | 776.59 | -1473.32 | FULL
G1 | 741.24 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -397.38 | -397.38 | 4563.08 | 741.62 | -1384.49 | FULL
G2 | 692.15 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -402.54 | -402.69 | 4573.51 | 692.52 | -1277.08 | FULL
G3 | 899.82 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -390 | -389.98 | 4634.15 | 898.74 | -1479.75 | FULL
G4 | 865.75 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -400.13 | -399.8 | 4562.32 | 866.11 | -1392.21 | FULL
G5 | 819.15 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -21.82 | -405.36 | -405.52 | 4572.63 | 819.49 | -1293.35 | FULL
G6 | 1100.11 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -387.71 | -387.69 | 4633.96 | 1098.94 | -1467.2 | FULL
G7 | 1075.79 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -398.76 | -398.75 | 4561.78 | 1076.04 | -1384.25 | FULL
G8 | 1036.09 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -406.17 | -406.17 | 4572.73 | 1036.37 | -1294.15 | FULL
G9 | 1478.7 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -391.52 | -391.54 | 4639.98 | 1478.61 | -1462.57 | FULL
G10 | 1488.91 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -21.85 | -408.7 | -408.44 | 4568.68 | 1490.38 | -1413.54 | FULL
G11 | 1441.12 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -21.82 | -413.4 | -413.05 | 4579.21 | 1440.52 | -1316.02 | FULL
G12 | 1469.02 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.02 | -425.26 | -425.23 | 4637.69 | 1469.12 | -1250.39 | FULL
G13 | 1379.09 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.02 | -424.52 | -424.48 | 4566.46 | 1378.55 | -1122.2 | FULL
G14 | 1293.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.02 | -423.96 | -423.93 | 4578.19 | 1292.46 | -998.91 | FULL
011R1WINTER09v5SNH