## 25F nomo
Covington-Maple Valley #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 017
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6658.414
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 773.22 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1799.28 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1329.24 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2029.65 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1799.28 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2326.69 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 997.9 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2915.68 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1535.91 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3378.12 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2029.65 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1329.24 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1301.72 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1535.91 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1808.37 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1808.37 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2326.69 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2371.55 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1867.47 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2932.15 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2371.55 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 773.22 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2915.68 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 997.9 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2448.19 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1301.72 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2932.15 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1867.47 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3378.12 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2448.19 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Covington-Maple Valley #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 017
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6338.7313
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1121.73 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2401.5 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1709.05 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2373.97 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2401.5 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2721.32 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1387.71 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3535.77 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 1923.53 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3551.33 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 775 | 2373.97 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1709.05 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1716.97 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1923.53 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2247.04 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2247.04 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2721.32 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2791.2 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2308.73 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3302.68 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2791.2 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1121.73 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3535.77 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1387.71 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2806.96 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1716.97 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 3302.68 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2308.73 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3551.33 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G13 | 1400 | 140 | 2806.96 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Covington-Maple Valley #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 017
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6060.2593
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1559.1 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2380.41 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2126.57 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2793.37 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2380.41 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3145.55 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 1832.7 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3448.92 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2304.59 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3000.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2793.37 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2126.57 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2010.78 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2304.59 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2614.75 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2614.75 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3145.55 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3180.44 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2660.14 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3085.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3180.44 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1559.1 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3448.92 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1832.7 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 3152.12 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2010.78 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 3085.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2660.14 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3000.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 3152.12 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Covington-Maple Valley #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 017
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4979.256
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2789.87 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2825.98 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2798.87 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2921.55 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2825.98 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2857.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2882.56 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3309.79 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 460 | 2892.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1828.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2921.55 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2798.87 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3051.09 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2892.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3068.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3068.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2857.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3146.62 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3308.13 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1934.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3146.62 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2789.87 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3309.79 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2882.56 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 2004.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3051.09 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1934.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3308.13 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1400 | 775 | 1828.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2004.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Covington-Maple Valley #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 017
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4635.17
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2658.67 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2443.51 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2680.82 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2568.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2443.51 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2777.35 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2533.1 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3077.82 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2545.26 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1594.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2568.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2680.82 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2733.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2545.26 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2744.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2744.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2777.35 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3060.16 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3038.23 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1693.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3060.16 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2658.67 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3077.82 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2533.1 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 1802.18 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2733.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1693.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3038.23 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1594.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1802.18 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Covington-Maple Valley #2 230kV Line (COV-CRES BYP @ COV)
G0 | 773.22 | 1121.73 | 1559.1 | 2789.87 | 2658.67
G1 | 1329.24 | 1709.05 | 2126.57 | 2798.87 | 2680.82 | Season/Year: | WINTER 2009
G2 | 1799.28 | 2401.5 | 2380.41 | 2825.98 | 2443.51 | Direction: | South-to-North (SN)
G3 | 997.9 | 1387.71 | 1832.7 | 2882.56 | 2533.1 | Case Loads: | Heavy Loads
G4 | 1535.91 | 1923.53 | 2304.59 | 2892.32 | 2545.26 | Outage: | 017
G5 | 2029.65 | 2373.97 | 2793.37 | 2921.55 | 2568.42 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 1301.72 | 1716.97 | 2010.78 | 3051.09 | 2733.64 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 1808.37 | 2247.04 | 2614.75 | 3068.42 | 2744.33 | Study Person: | FRP9899
G8 | 2326.69 | 2721.32 | 3145.55 | 2857.71 | 2777.35 | Source: | 017WINTER09v1SNH
G9 | 1867.47 | 2308.73 | 2660.14 | 3308.13 | 3038.23
G10 | 2371.55 | 2791.2 | 3180.44 | 3146.62 | 3060.16
G11 | 2915.68 | 3535.77 | 3448.92 | 3309.79 | 3077.82
G12 | 2448.19 | 2806.96 | 3152.12 | 2004.68 | 1802.18
G13 | 2932.15 | 3302.68 | 3085.56 | 1934.25 | 1693.25
G14 | 3378.12 | 3551.33 | 3000.9 | 1828.22 | 1594.1
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 017 | Covington-Maple Valley #2 230kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6658.414 | 773.22 | 1329.24 | 1799.28 | 997.9 | 1535.91 | 2029.65 | 1301.72 | 1808.37 | 2326.69 | 1867.47 | 2371.55 | 2915.68 | 2448.19 | 2932.15 | 3378.12
35F | 6338.7313 | 1121.73 | 1709.05 | 2401.5 | 1387.71 | 1923.53 | 2373.97 | 1716.97 | 2247.04 | 2721.32 | 2308.73 | 2791.2 | 3535.77 | 2806.96 | 3302.68 | 3551.33
45F | 6060.2593 | 1559.1 | 2126.57 | 2380.41 | 1832.7 | 2304.59 | 2793.37 | 2010.78 | 2614.75 | 3145.55 | 2660.14 | 3180.44 | 3448.92 | 3152.12 | 3085.56 | 3000.9
60F | 4979.256 | 2789.87 | 2798.87 | 2825.98 | 2882.56 | 2892.32 | 2921.55 | 3051.09 | 3068.42 | 2857.71 | 3308.13 | 3146.62 | 3309.79 | 2004.68 | 1934.25 | 1828.22
70F | 4635.17 | 2658.67 | 2680.82 | 2443.51 | 2533.1 | 2545.26 | 2568.42 | 2733.64 | 2744.33 | 2777.35 | 3038.23 | 3060.16 | 3077.82 | 1802.18 | 1693.25 | 1594.1

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 772.8 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 521.07 | 521.12 | 6675.69 | 773.22 | -627.04 | FULL
G1 | 1329 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 520.29 | 520.37 | 6621.93 | 1329.24 | -923.62 | FULL
G2 | 1799.31 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 512.17 | 512.06 | 6651.33 | 1799.28 | -1162.11 | FULL
G3 | 997.47 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 517.55 | 517.45 | 6676.98 | 997.9 | -696.64 | FULL
G4 | 1535.65 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 523.1 | 523.04 | 6622.62 | 1535.91 | -980.79 | FULL
G5 | 2029.93 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 512.52 | 512.43 | 6653.65 | 2029.65 | -1228.73 | FULL
G6 | 1301.57 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 516.92 | 516.99 | 6678.04 | 1301.72 | -748.35 | FULL
G7 | 1808.21 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 514.06 | 514.11 | 6624.13 | 1808.37 | -1019.44 | FULL
G8 | 2326.72 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 513.22 | 513.17 | 6655.51 | 2326.69 | -1289.32 | FULL
G9 | 1867.61 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 517.82 | 517.88 | 6686.98 | 1867.47 | -864.11 | FULL
G10 | 2371.81 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 514.17 | 514.22 | 6635.06 | 2371.55 | -1145.36 | FULL
G11 | 2916.11 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 522.31 | 522.41 | 6667.95 | 2915.68 | -1421.03 | FULL
G12 | 2447.79 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 523.88 | 523.84 | 6698.34 | 2448.19 | -1042.46 | FULL
G13 | 2932.45 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 523.08 | 523.04 | 6647.76 | 2932.15 | -1303.62 | FULL
G14 | 3376.41 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 519.75 | 519.66 | 6680.24 | 3378.12 | -1539.85 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1121.33 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 501.01 | 501.1 | 6351.23 | 1121.73 | -797.46 | FULL
G1 | 1708.69 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 504.83 | 504.86 | 6301.66 | 1709.05 | -1107.3 | FULL
G2 | 2401.79 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.67 | -494.95 | -494.87 | 6336.03 | 2401.5 | -1490.64 | FULL
G3 | 1387.9 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 502.55 | 502.5 | 6354 | 1387.71 | -885.34 | FULL
G4 | 1923.5 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 499.75 | 499.68 | 6302.9 | 1923.53 | -1166.79 | FULL
G5 | 2374.11 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 498.23 | 498.18 | 6335.54 | 2373.97 | -1395.93 | FULL
G6 | 1716.71 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 506.69 | 506.76 | 6356.25 | 1716.97 | -954.89 | FULL
G7 | 2247.14 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 499.84 | 499.95 | 6305.95 | 2247.04 | -1233.45 | FULL
G8 | 2721.53 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 507.38 | 507.45 | 6340.11 | 2721.32 | -1476.47 | FULL
G9 | 2309.01 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 506.62 | 506.66 | 6366.97 | 2308.73 | -1090.4 | FULL
G10 | 2791.43 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 508.5 | 508.57 | 6316.86 | 2791.2 | -1339.95 | FULL
G11 | 3536.15 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2596.28 | -2596.31 | 6357.13 | 3535.77 | -1745.67 | CTG_FAIL_IN_FULL
G12 | 2807.84 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 509.13 | 509.17 | 6377.89 | 2806.96 | -1225.59 | FULL
G13 | 3303.01 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 508.49 | 508.58 | 6331.03 | 3302.68 | -1484.71 | FULL
G14 | 3551.84 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3516.94 | 3519.38 | 6347.42 | 3551.33 | -1605.23 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1559.37 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 493.96 | 494.02 | 6081.11 | 1559.1 | -1035.49 | FULL
G1 | 2126.69 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 494.65 | 494.74 | 6033.02 | 2126.57 | -1322.2 | FULL
G2 | 2380.67 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.67 | -485.1 | -484.85 | 6049.47 | 2380.41 | -1439.95 | FULL
G3 | 1832.85 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 494.21 | 494.14 | 6083.81 | 1832.7 | -1117.23 | FULL
G4 | 2304.75 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 492.86 | 492.91 | 6033.76 | 2304.59 | -1369.96 | FULL
G5 | 2793.71 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.67 | -485.56 | -485.47 | 6062.5 | 2793.37 | -1633.48 | FULL
G6 | 2011.06 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 488.48 | 495.35 | 6083.27 | 2010.78 | -1099.13 | CTG_FAIL_IN_FULL
G7 | 2614.84 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 488.3 | 488.35 | 6037.33 | 2614.75 | -1428.59 | FULL
G8 | 3146 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2535.66 | -2535.49 | 6066.6 | 3145.55 | -1707.81 | CTG_FAIL_IN_FULL
G9 | 2660.24 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 496.46 | 496.55 | 6095.32 | 2660.14 | -1279.32 | FULL
G10 | 3180.8 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 496.43 | 496.39 | 6048.32 | 3180.44 | -1546.94 | FULL
G11 | 3449.06 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2534.88 | -2534.77 | 6063.07 | 3448.92 | -1686.08 | CTG_FAIL_IN_FULL
G12 | 3152.47 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.59 | 489.52 | 489.45 | 6104.26 | 3152.12 | -1424.88 | FULL
G13 | 3086.01 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -435.69 | -435.65 | 6027.69 | 3085.56 | -1340.88 | FULL
G14 | 3001.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -436.03 | -435.82 | 6034.36 | 3000.9 | -1261.96 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2790.32 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2410.26 | -2409.93 | 5037.02 | 2789.87 | -1630.15 | CTG_FAIL_IN_FULL
G1 | 2798.76 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2399.15 | -2398.85 | 4966.99 | 2798.87 | -1597.5 | CTG_FAIL_IN_FULL
G2 | 2827.22 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2411.34 | -2410.5 | 4977.56 | 2825.98 | -1592.71 | CTG_FAIL_IN_FULL
G3 | 2882.81 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2411.1 | -2410.83 | 5034.32 | 2882.56 | -1637.59 | CTG_FAIL_IN_FULL
G4 | 2892.79 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2406.26 | -2405.93 | 4964.14 | 2892.32 | -1597.11 | CTG_FAIL_IN_FULL
G5 | 2922.03 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2410.41 | -2410.16 | 4975.32 | 2921.55 | -1585.08 | CTG_FAIL_IN_FULL
G6 | 3051.38 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2399.55 | -2399.39 | 5032.15 | 3051.09 | -1616.23 | CTG_FAIL_IN_FULL
G7 | 3068.85 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2391.21 | -2390.49 | 4962.54 | 3068.42 | -1583.57 | CTG_FAIL_IN_FULL
G8 | 2858.18 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2219.37 | -2219.26 | 4967.8 | 2857.71 | -1417.96 | FULL
G9 | 3308.54 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3278.57 | 3279.09 | 5029.82 | 3308.13 | -1539.81 | FULL
G10 | 3147.18 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2221.97 | -2220.99 | 4956.78 | 3146.62 | -1419.02 | FULL
G11 | 3310.2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3280.71 | 3278.09 | 4970.99 | 3309.79 | -1480.31 | FULL
G12 | 2004.85 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -424.03 | -423.91 | 4980.8 | 2004.68 | -626.11 | FULL
G13 | 1936.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -426.29 | -426.27 | 4910.38 | 1934.25 | -552.78 | FULL
G14 | 1828.12 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -425.36 | -425.3 | 4922.23 | 1828.22 | -459.58 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2658.58 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2298.28 | -2297.95 | 4692.89 | 2658.67 | -1516.28 | CTG_FAIL_IN_FULL
G1 | 2682.73 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2306.94 | -2306.34 | 4622.25 | 2680.82 | -1508.15 | CTG_FAIL_IN_FULL
G2 | 2445.67 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2125.86 | -2124.58 | 4628.94 | 2443.51 | -1342.57 | FULL
G3 | 2533.41 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2146.47 | -2147.39 | 4684.32 | 2533.1 | -1388.14 | FULL
G4 | 2545.56 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2136.35 | -2137.97 | 4615.73 | 2545.26 | -1357.38 | FULL
G5 | 2567.81 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2149.69 | -2150.64 | 4626.06 | 2568.42 | -1344.92 | FULL
G6 | 2736.09 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2148.5 | -2146.54 | 4683.69 | 2733.64 | -1376.59 | FULL
G7 | 2746.72 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2142.78 | -2143.39 | 4613.97 | 2744.33 | -1352.41 | FULL
G8 | 2779 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2154.51 | -2152.81 | 4627.01 | 2777.35 | -1341.53 | FULL
G9 | 3040.36 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2140.85 | -2139.2 | 4685.52 | 3038.23 | -1346.29 | FULL
G10 | 3060.58 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2151.97 | -2150.61 | 4615.76 | 3060.16 | -1337.6 | FULL
G11 | 3080.13 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2145.14 | -2143.59 | 4629.11 | 3077.82 | -1308.9 | FULL
G12 | 1802.69 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -424.79 | -424.73 | 4642.77 | 1802.18 | -477.98 | FULL
G13 | 1695.17 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -422.75 | -422.72 | 4573.2 | 1693.25 | -375.79 | FULL
G14 | 1593.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -423.17 | -423.13 | 4586.33 | 1594.1 | -293.25 | FULL
017WINTER09v1SNH