# Comments from the Beams Division Review of the Kicker Flourinert Cooling System

# June 14, 2002

# Chaired by Maurice Ball

## System Specifications

## Presenter:  S. Reeves

- (Reviewer:  B. Ducar)  From my limited knowledge of fluid process systems, the design appeared to be quite thorough and well documented.  I especially appreciate identification of variables to be monitored by ACNET.  Some amount of additional effort might be required to consolidate (sum) significant status points as a "permit" to Jensen's kicker system.

- (Reviewer:  B. Ducar)  I have heard that the necessity of the back-up pump was questioned.  I believe that it should remain in the design and note that back-up pumps are included in all or most all of the process water systems already planned for NuMI.  Failure of a single pump could significantly affect operations.

- (Reviewer:  B. Ducar)  A total of 11 variables are indicated for ACNET monitoring.  Some thought might be given as to which of these, if any, might be monitored by the Beam Permit System.

- (Reviewer:  D. Pushka)  On subject of Pressure gages, the bill of materials indicate glycerin filled gauges.  These are applicable for use where pressure fluxuations would cause the needed to vibrate.  This should not be the case in thissystem and their use is rightly questioned.  Apparently, the group mis-interprets glycerin filled gauges as being good quality and non-glycerin filled gauges as being poor quality.  I agree the little non-glycerin filled gauges in the stock room are crap, but there are good quality non-glycerin filled gauges.  Use one.

- (Reviewer:  D. Pushka)  Use thermowells for the temperature instruments.  Or just locate the sensor on the pipe wall, under the insulation.

- (Reviewer:  D. Pushka)  Do not design a pressure vessel with flat ends.  Buy pipe caps and assemble using qualified welders so that a MAWP can be calculated.

- (Reviewer:  D. Pushka)  The specification 1320-ES-296363 is not a specification as one would attach to a purchase order.  It is an engineering note and should be labeled as such.

- (Reviewer:  D. Pushka)  Get the voltage correct in the "specification 1320-ES-296363".  To use a variable speed drive (VSD), the motors need to be 3 phase.  Hitachi makes some pretty affordable 460 VAC drives for 5 HP motors for $450. I would avoid the complexity of attempting feedback control on the pressure by using the VSD.  Rather, set it to get the right flow thru the load resistors and then remove the setting knob.

- (Reviewer:  D. Pushka)  On the "specification 1320-ES-296363", there is a sentance about having the operation point for the system be at or to the left of the "best efficiency point of the pump" is silly.  There is little technical reason for doing this on a pump operated at a single frequency, let alone one on a VSD.

- (Reviewer:  D. Pushka)  On the Tubing materials, I would specify an all welded tubing system except for compression fittings at the spools where attachments are made to the load assemblies and at the "skid" upstairs.  A competent contractor should have the required automated tube welder or can lease it for the job.  If the contractor can't or is reluctant to, then we don't want them on our job.

- (Reviewer:  D. Pushka)  List the setpoints for the alarms, interlocks.

- (Reviewer:  D. Pushka)  If the heater is needed, can it just be heat tracing cable attached to the outside of the tubing?  This will greatly reduce the energy transfer rate per unit area to small values, avoids adding another component into the system (no additional leak potential) and can be added later w/o breaking into the system.

- (Reviewer:  R. Reilly)  Here are my comments on the Fluorinert Cooling System:

  - Expansion Tank:  FESHM 5031 requires an ASME Code stamped vessel or director's exemption if the vessel falls within the scope of ASME Code Section VIII; see Div. 1 paragraph U-1. Vessels outside the scope include: ID not to exceed 6" with no limit on length, or MAWP not to exceed 15 psig.  I'm unhappily surprised that there isn't something suitable on the market that you could get off the shelf. Have you tried suppliers for the dairy and food processing industry?  You could even make it out of a length of 4" Sch 10S pipe and two pipe caps and a bunch of threadolets. Same with the overflow recovery tank. I think I have some leftover pipe caps.  Do you have a filling port somewhere? I suppose it will be at the top of the expansion tank. The recovery tank will need a low pressure vent to atmosphere or you'll dead head it. It would not have to be code then, either. Should this tank be upstairs? You could then run a line from it to the expansion tank and refill just by opening valves.

  - Tubing quality:  I had leakage of Fluorinert when I used ordinary stainless tubing and Swagelok fittings on the top of my TeV kicker pulsers, and the fittings galled when I overtightened them trying to stop the leaks. This was with just 6" of head pressure. I ended up doing an overkill, getting polished tubing and welding the fittings. I think I would not have had this problem if I had used polished tubing to begin with. I have some of the failed ones if you want to look them over.

  - Pipe Threads in Ball Valves:  I think it is perfectly reasonable to use NPT to compression unions and weld them into the valves if it saves a lot of money.

  - Flow Meters:  You show a flow indicator. Do you need a flow meter?

- (Reviewer:  R. Reilly)  I think the system looks good. You might consider putting it all on a skid like Ross does with his RAW systems.

- (Reviewer:  J. Riordan)  There are about a dozen sensors that measure process parameters for the system. The designer should consider the cost of the cable, connectors, and the cost of the labor required to pull and terminate the cables.

- (Reviewer:  J. Riordan)  The Powers 535 is not capable of powering all the process parameter sensors. Therefore, an instrumentation chassis or some module will have to be built.

- (Reviewer:  J. Riordan)  The Powers 535 can handle a remote temperature set point if desired.

- (Reviewer:  J. Riordan)  A temperature sensor on the return line for the CHW after the heat exchanger or a temperature sensor on the Fluorinert line before the heat exchanger would help monitor the heat exchanger performance.

- (Reviewer:  J. Riordan)  A strainer with a low micron rating in addition to or in place of the 5 micron filter on the CHW should be considered. This would maximize the interval between filter change outs and minimize maintenance time.

- (Reviewer:  J. Riordan)  I would recommend measuring the temperature of the Fluorinert with RTDs that can be epoxied to the pipe under the insulation. Since the temperature control (+/- 3 F) range is not incredibly narrow, the better accuracy of a RTD in a thermowell is not required. Also, the thermowells would be additional, unnecessary leak paths.

- (Reviewer:  J. Riordan)  Pressure is an important parameter for the system. Consider using pressure gages with compression fittings to minimize the threaded joints and the potential leak paths. Also, Noshok pressure transmitters are high quality and have been used successfully at the laboratory – non-threaded connections might be available.

- (Reviewer:  K. Williams)  The excess use of gauges and valves in the filter line is to be commended.  Often, filter lines are equipped with isolation valves at each end only. And, although having pressure gauges between each filter is very good practice from a diagnostic point of view, they are sometimes excluded due to cost.  Changing a single filter can easily dump 1/4 to 1/2 gallon of fluid. A series of filters in a row, unisolated by valves, can dump more, even if only one filter in the series is opened. If it is necessary to open and check each of the filters, wastes go up. At $400 per gallon, Fluorinert is a very costly fluid. The losses experienced on the very first access of the filters for service and maintenance can more than pay for the minimal added expense of the two extra valves and gages in the filter line.

- (Reviewer:  K. Williams)  Somewhat cheaper, reliable glycerin gauges are available. This cost may be reduced by 20 to 30% if buying in quantity, from a total of $1500 to say $1100 or $1200. The caution here is, you get what you pay for. In the LCW group’s extensive experience, cheap gauges such as those stocked by the Fermilab stockroom, unfilled and smaller in size, do not have the quality, reliability or service life to support their use.  Also, one vendor, Swagelok, has introduced a new line of gauges that are connected via tube stubs and compression fittings instead of 1/4” NPT threaded joints. Although I do not have current pricing, they may be a good way to compromise between the need for information, and the concern of NPT joints leaking Fluorinert.

- (Reviewer:  K. Williams)  Although the CHW lines are piped through the length of the MI-60 gallery in stainless steel, from the point where the Fluorinert skids will tap into them could be a cheaper material. Carbon steel, or even hard piped copper could be used.  This could substantially reduce the costs of piping materials.

- (Reviewer:  K. Williams)  In the review meeting, I had spoken up about the temperature control valve placement before the heat exchanger. Upon further study, its placement in the CHW supply line to the heat exchanger looks fine to me. There are two schools of thought here, the first, that placing it after the exchanger helps ensure the exchanger stays flooded, the second, that placement after the unit submits the unit to undue pressure load. In this use, the lines returning from the exchanger to the CHW system are long, and above the exchanger, and it should easily remain fully flooded after initial fill.

## System P&ID

## Presenter:  S. Reeves

- (Reviewer:  D. Pushka)  The P&ID drawings and the layout drawings are not signed off.  They should be signed off and formal revisions made when the design changes.

- (Reviewer:  D. Pushka)  On the P&ID, since this is a cooling system, include the temperatures in the legend.  Also show the heat loads.

- (Reviewer:  D. Pushka)  On the P&ID, there are a heck of a lot of bits of instrumentation, everyone is a possible leak source due to the threaded connections.  Reduce the number to the bare minimum needed and epoxy them in.

- (Reviewer:  D. Pushka)  P&ID should indicate the chilled water flow.

- (Reviewer:  D. Pushka)  P&ID should indicate carbon steel piping for the chilled water.

- (Reviewer:  D. Pushka)  P&ID should move the 7 gallon overflow tank to upstairs and get it out of the tunnel. Reduce the set pressure of the relief valve accordingly.

- (Reviewer:  D. Pushka)  P&ID shows 31 ball valves in fluorinert service.  Are all of these really needed?  Every one is a potential leak.  Consider using the bellows sealed Nupro valves as the isolation for the pressure gauges.

- (Reviewer:  D. Pushka)  P&ID should indicate a set presure on the relief valve.

## Cost Estimate

- (Reviewer:  B. Ducar)  A comment relative to fixed price vs T&M.  There are clear yet different advantages to these two methods of getting work done.  Supervision by the Task Manager is especially critical to getting T&M work performed efficiently.  As Childress has pointed out, choice of T&M can minimize EDIA.  Another consideration is that shorter and unpredicted shutdowns are more amenable to T&M.  Generalities aside, the choice is nonetheless quite subjective.

- (Reviewer:  D. Pushka)  Since the cost estimate currently exceeds the budget, the system needs to be slimmed down (remove hot spare pump, reduce instrumentation, etc.) to get the cost in line with the budget.

- (Reviewer:  D. Pushka)  Remove all spare parts from the cost estimate.  Spares are to be paid for out of the operation budget, not the plant line budget.

- (Reviewer:  D. Pushka)  Complete the piping layout drawings and plan on executing this work as a fixed price contract.  This adds drafting costs at about $30 per hour but saves pipe fitter costs for a two man crew of $120 per hour.  Which is more economical, paying a draftsman to work out the routing details to avoid interferences or paying a piping crew to do the same?  Using the formar also allows the routing to be documented and to be shared with others who have devices in the tunnel.

- (Reviewer:  K. Williams)  In my experience, this project is at the dividing line between which method, T & M or fixed-price, would be best. If all necessary drawings, specifications, bids and permits can be acquired in time that this project can be part and parcel of a larger package, and that the timeline of the project does not suffer, I think the fixed price bids method would be prudent.  If, however, there is not a suitable larger package this can ride on, and / or the deadlines cannot be met, T&M may be the wisest choice. Although I have heard much criticism concerning T&M crews not having motivation, in my extensive experience, the current crews at Fermilab can and do provide competent and sufficiently expedient work for many small or miscellaneous projects, enough so to offset some of the extra time, work, and hassles of running a bid package through the system.