Eastern Interconnection Phasor Project

Performance Requirements Task Team (PRTT)

A Guide for PMU Installation, Commissioning and Maintenance

Part I

PMU Acceptance Test Checklist

for Connecting to TVA SuperPDC

April 28, 2006

Last Updated: May 8, 2006

Performance Requirements Task Team Leader:

Damir Novosel, KEMA

Task Force Contributors:

Ken Martin, BPA – Task Force Leader

Ritchie Carroll, TVA

Henry Huang, PNNL, CERTS

Virgilio Centeno, Virginia Tech

Damir Novosel, KEMA

Yi Hu, KEMA

(Others to be added)

Revision History

| Date | Rev. # | Description |
| --- | --- | --- |
| 04/24/06 | 1 | Development started. |
| 05/08/06 | 1.1 | Reviewed and revised per teleconference 5/5/06 |

Table of Contents

1.	Glossary of Terms	4

2.	Preface	5

3.	PMU Acceptance Test for Connecting to TVA SuperPDC	5

4.	Checklist of PMU Acceptance Test for Connecting to TVA SuperPDC	5

5.	Concluding Remarks	6

6.	Appendix I: TVA PMU Connection Tester	8

7.	Appendix II: TVA IEEE C37.118 Proxy Service	10

List of Figures

Figure 1  PMU Connection Test Tool with IEEE C37.118 selected	8

Figure 2  PMU Connection Test Tool with IEEE 1344 selected	9

Figure 3  Data flow diagram of the Proxy Service	10

# Glossary of Terms

BPA/PDCStream – An extension of IEEE 1344, widely used by the BPA PDC and human-machine interface software on the West Coast.

GPS – Global Positioning System. A satellite based system for providing position and time. The accuracy of GPS based clocks can be better than 1 microsecond.

IEEE 1344 – A highly efficient protocol for real time SynchroPhasor data. Typically data is streamed in this format over UDP/IP or across a serial link.

IEEE C37.118 – Related to IEEE 1344, but adds much needed capability. This protocol and its associated standard are intended to replace IEEE 1344 and the BPA/PDCStream protocols. Typically data is streamed in this format over UDP/IP or across a serial link.

NERC – North American Electricity Reliability Council

PDC – Phasor Data Concentrator. A logical unit that collects phasor data, and discrete event data from PMU’s and possibly from other PDC’s, and transmits data to other applications. PDC’s may buffer data for a short time period but do not store the data.

PMU – Phasor Measurement Unit. A device that samples analog voltage and current data in synchronism with a GPS-clock. The samples are used to compute the corresponding phasors. Phasors are computed based on an absolute time reference (UTC), typically derived from a built-in GPS receiver.

SuperPDC – The PDC which is implemented to collects all the phasors of the Eastern Interconnection for the EIPP. It is physically located at TVA.

TCP/IP – TCP/IP is a low-level protocol for use mainly on Ethernet or related networks. Most of the higher-level protocols use TCP/IP to transport the data. TCP/IP provides a highly reliable connection over unreliable networks, using checksums, congestion control, and automatic resending of bad or missing data. TCP/IP requires time to handshake new connections and will block if missing data is being resent.

TVA – Tennessee Valley Authority

UDP/IP – UDP/IP is a low-level IP protocol that provides low-latency communication across Ethernet or related networks. UDP/IP does not provide any error-control or resending of missing or bad data. The Application will need to check data for correctness. UDP/IP however, does not require time for handshaking and will not block, making it ideal for real-time data communications.

UTC – Coordinated Universal Time (initials order based on French). UTC represents the time-of-day at the Earth's prime meridian (0° longitude).

# Preface

This document intends to serve as a guide for connecting PMUs to TVA’s SuperPDC. Before a PMU can be connected to the SuperPDC and function properly, several tests need to be performed as detailed in the remainder of this document.

# PMU Acceptance Test for Connecting to TVA SuperPDC

This document is focused only on the series of tests performed prior to connecting a PMU to the SuperPDC. Actually PMU acceptance test is a broad topic and the checklist in this document is only a subset of it. Acceptance tests should be performed when a PMU is commissioned to service. The PMU acceptance tests include normal hard wiring check, insulation test, calibration and functional tests to ensure that hard wire connections are good, insulation meets substation requirements, input signals are properly calibrated and the device is still operational. For PMU devices, there are several additional things need to be checked: designated A phase (it should be the same across the whole EIPP system), phase sequence (ABC, not ACB), and GPS reception. All these are beyond the scope of this document. But this document can evolve to become a PMU commissioning guide which will address PMU acceptance more broadly.

# Checklist of PMU Acceptance Test for Connecting to TVA SuperPDC

The intention of this section is to list the tests which need to be performed before connecting the PMU to the SuperPDC. Examples of test methods are introduced but they are not the only methods and this list does not intend to provide detailed test methods and test setup. Users should apply the checklist to their respective situations with their own available resources.

Network Connectivity Test

This refers to the data link between a PMU and the SuperPDC. The data link can be a dedicated data line, a dial-up link, LAN-LAN VPN, etc. Tests in this section will include using the “ping” command to determine connection and presence of devices at each end and a data rate test to assure that the connection has sufficient capacity to carry the required data. It should be pointed out that many currently used firewalls and other security elements do not respond to “ping”.  This makes network connectivity difficult to verify in some cases. It is suggested to use the PMU Connection Test Tool as detailed in Appendix I to verify the network connectivity.

Protocol Test (TCP/IP or UDP/IP)

The PMU-PDC communication will be by TCP/IP or UDP/IP.  Once the parameters are determined, the connection with the SuperPDC can be tested.  If it works, the protocol is probably ok.  If not, further investigation is required.  In both cases, a monitor, such as Ethereal (free download at www.ethereal.com) or UDP Listener (free download at ???), should be used to be sure the protocol guidelines are implemented correctly. TVA PMU Connection Test Tool (see Appendix I) tests protocols and data formats. If the Tool is used, this protocol test can be combined with the data format test below.

Data Format Test (IEEE 37.118, PDCStream, IEEE 1344, OPC, etc.)

Once the format is determined, the connection with the SuperPDC can be tested.  If it works, the format is probably ok.  If not, further investigation is required.  All commands used in the IEEE protocol should be tested with a close examination of the data to be sure it fully conforms.  A monitor, such as Ethereal, provides a good tool to allow precise examination of the data to assure conformance. Ritchie Carroll of TVA developed a PMU Connection Test Tool (see Appendix I), which can be used to test both protocols and data formats. This tool can be downloaded from the EIPP Tools website http://phasors.pnl.gov/resources_tools.html. For IEEE C37.118 data format, configuration frames are sent when requested if TCP/IP is used. For UDP/IP, Ritchie developed an IEEE C37.118 Proxy Service application, which requests configuration frames once every minutes. This service also make PMUs secure. Details about this Service application can be found in Appendix II. This Proxy Service application is free for download at the EIPP Tools website http://phasors.pnl.gov/resources_tools.html.

Reporting Data Rate test

Verify the reporting rate as it is supposed to be (e.g. 30 samples-per-second). It is suggest to use the PMU Connections Test tool (see Appendix I) for this test.

Latency Test

Latency can be roughly determined from the difference between the timestamp and the time when the data arrives at the SuperPDC. Currently for EIPP PMUs, latency is typically 1~5 seconds. It is suggested to use the PMU Connection Test Tool (see Appendix I) to measure the latency.

# Concluding Remarks

This checklist is developed in the intention of facilitating PMU connection to the SuperPDC. There are often questions about how to connect PMUs to the SuperPDC and it has been a critical path for EIPP to bring phasor data into EIPP real-time data stream. Hopefully this checklist can serve as a starting point. This checklist is by no means a complete one, and it will be updated when new situations come up. Comments and suggestions are welcome and should be directed to:

Ken Martin, kemartin@bpa.gov

Or Ritchie Carroll, jrcarrol@tva.gov

PMU data communication involves many aspects. The EIPP Data Management Task Team led by Paul Myrda maintains a frequently asked questions (FAQ) site http://phasors.pnl.gov/resources_data.html. Please refer to that site for more information on data communication.

With a broader scope, this checklist may evolve to become a PMU commissioning guide, of which the checklist is only a subset.

# Appendix I: TVA PMU Connection Tester

This tool is developed by Ritchie Carroll of TVA for testing connections between PMUs and PDCs. It can test various data formats including IEEE C37.118, IEEE 1344, etc. This tool can be downloaded from the EIPP Tools website http://phasors.pnl.gov/resources_tools.html.

Figure 1  PMU Connection Test Tool with IEEE C37.118 selected

Figure 2  PMU Connection Test Tool with IEEE 1344 selected

# Appendix II: TVA IEEE C37.118 Proxy Service

This IEEE C37.118 Proxy Service is developed by Ritchie Carroll of TVA. The purpose of this Windows service based application is to provide a “proxied” data stream in native IEEE C37.118 format from a PMU or PDC device at a utility without having to expose its internal substation devices through an external connection. Figure 3 shows the data flow of this Proxy Service. This service application can be downloaded at the EIPP Tools website http://phasors.pnl.gov/resources_tools.html. The source code is also included to allow utilities and vendors to establish trust in what data processing steps the application is performing, but is solely owned and copyrighted by TVA and is being provided exclusively for purposes in conjunction with the Eastern Interconnect Phasor Project, any other use of source code would have to be approved by TVA.

Figure 3  Data flow diagram of the Proxy Service

After installation, the service will need to be started to create the initial configuration file (“C37.118 Proxy Service.exe.config”) – make sure to stop the service before making modifications to the configuration file.  The configuration file defines the settings needed for rebroadcast of the PDC/PMU data streams.  Below is an example – note that you can define as many connections as needed (i.e., one per PMU or PDC).  Note that the destination port per given IP will need to be unique – you will need to work with TVA to select an appropriate non-used port number for destinations pointing into the private EIPP hosting network:

  - Example configuration file for the Proxy Service

<?xml version="1.0" encoding="utf-8"?>

<configuration>

<appSettings file="">

<clear />

<!-- Define the total number of connections handled by proxy service -->

<add key="TotalProxyConnections" value="2" />

<!-- The section below begins definition of first connection -->

<add key="ProxyConnection1.Name" value="Example PDC Connection" />

<add key="ProxyConnection1.Host" value="165.233.31.32" />

<add key="ProxyConnection1.Port" value="5000" />

<add key="ProxyConnection1.PmuID" value="1" />

<!-- This example defines two destinations for PDC output, allowing data transmission to more than one location -->

<add key="ProxyConnection1.Destinations" value="127.0.0.1:3200,152.85.98.5:3200" />

<add key="ProxyConnection1.LogFileName" value="D:\apps\IEEE C37.118 Data Proxy Service\My PDC Connection.log" />

<!-- The section below begins definition of second connection -->

<add key="ProxyConnection2.Name" value="Example PMU Connection" />

<add key="ProxyConnection2.Host" value="165.233.31.15" />

<add key="ProxyConnection2.Port" value="4712" />

<add key="ProxyConnection2.PmuID" value="3" />

<add key="ProxyConnection2.Destinations" value="152.85.98.5:3300" />

<add key="ProxyConnection2.LogFileName" value="D:\apps\IEEE C37.118 Data Proxy Service\My XYZ PMU Connection.log" />

</appSettings>

</configuration>