July 22, 1994

Contract #TW0592

SPECIAL STANDARD SPECIFICATION

SECTION 16921-S

VARIABLE FREQUENCY DRIVE FOR VARIABLE

TORQUE PUMP OR FAN ALTERNATING CURRENT MOTORS

Page

PART 1 - GENERAL

1.01	Description of Work	2

1.02	References	2

1.03	Submittals	2

1.04	Quality Assurance	3

1.05	Warranty	3

PART 2 - PRODUCTS

2.01	General	3

2.02	VFD Supplied With A New Pump or Fan System	4

2.03	VFD Supplied For An Existing Pump or Fan System	4

2.04	VFD Maximum Voltage & Current Harmonic Distortion	5

2.05	Design Features	5

2.06	Protective Features	7

2.07	Diagnostic Fault Indicators	7

2.08	VFD Environmental and Service Conditions	8

2.09	Spare Parts	8

2.10	VFD Motor Requirements	8

PART 3 - EXECUTION

3.01	Examination	9

3.02	Preparation	9

3.03	Installation	9

3.04	Field Quality Control	9

SPECIAL STANDARD SPECIFICATION

SECTION 16921-S

VARIABLE FREQUENCY DRIVE FOR VARIABLE

TORQUE PUMP OR FAN ALTERNATING CURRENT MOTORS

PART 1 - GENERAL

1.01	Description of Work

A.	The Contractor shall furnish and install a complete Variable Frequency Drive (VFD) System as described in this specification and as detailed on the construction drawings.  The VFD will be used to control the speed of a variable torque, pump or fan alternating current (A.C.) motor.

B.	The Contractor shall be responsible for the installation, field testing, and startup of the equipment covered by this specification.

1.02	REFERENCES

The requirements of the most current versions of the codes, standards, and other documents referenced in this document are to be considered as part of this specification.  In the event of a conflict between this specification and referenced documents or between several referenced documents, the more stringent requirement shall be followed.

A.	Construction drawings included with this contract.

B.	Sandia National Laboratories (SNL) standard specifications.

1.	Section 01300 -- Descriptive submittals.

2.	Section 16001 -- Electrical work.

3.	Mechanical Specifications issued with this contract.

C.	The following codes and standards are referenced:

NEMA -- National Electrical Manufacturers' Association

NEC  -- National Electrical Code NFPA-70

IEEE -- Institute of Electrical and Electronic Engineers

UL   -- Underwriters Laboratories

ANSI -- American National Standards Institute

1.03	Submittals

A.	The submittal requirements of the SNL Standard Specification, Section 01300 shall be followed.

B.	The Contractor shall submit the final documentation for the VFD installation as described in Section 3.03 of this specification.

C.	Final Drawings:  The VFD supplier shall furnish one set of "as-built" reproducible drawings on black on white mylar 22 X 34 inch (56 X 85 cm) size showing dimensions, details, wiring diagrams and interconnections.  All wiring on all systems shall be included on these drawings.  Drawings shall be of sufficiently high quality drafting and reproduction to permit microfilming.  Internal wiring diagrams shall be laid out such that terminal blocks for external connections have sufficient room, a minimum of one and one-half inch, for showing cables for external connections.  In addition to the above specific design drawings, the VFD supplier shall furnish complete sets of their standard drawings showing control schematics, transistor schematics, wiring, outline dimensions, mounting details, and equipment weight.

D.	Instruction Books and Spare Parts List:  VFD supplier shall furnish copies of all instruction books, spare parts lists, and special bulletins covering on-site storage.

E.	Filter Requirements:  The VFD supplier shall provide documentation from the VFD manufacturer per Section 2.05 M to meet the maximum noise requirements per Section 2.04.

1.04	QUALITY ASSURANCE

A.	The VFD manufacturer shall have a minimum of five years in designing and manufacturing VFDs of the horsepower, range, and technology specified herein.

B.	The Contractor shall arrange and pay for the services of the VFD manufacturers' service engineer to train SNL's personnel in proper operation and maintenance of the VFD system.  Provide a minimum of two (2) normal eight-hour working days on-site instruction unless otherwise noted.

1.05	Warranty

If any defect in apparatus supplied, or failure to comply with this specification shall appear within the period of one (1) year from the date of commercial operation, not to exceed 42 months from shipment, the VFD shall be immediately repaired. The Contractor shall correct, without delay and at his own expense, the defects or failure of compliance by repairing the defective parts, by supplying a non-defective replacements, or by correcting a defective or deficient design.

PART 2 - PRODUCTS

2.01	General

A.	The VFD shall be U.L. listed.

B.	The VFD shall comply with the latest applicable standards of:

1.	ANSI.

2.	IEEE.

3.	NEMA.

C.	The VFD shall be of a fixed Direct Current (D.C.) bus type with a full wave input diode bridge.  The VFD shall convert three-phase, 60 Hz, input power to three-phase adjustable voltage, adjustable frequency output power using Pulse Width Modulation (PWM) switching techniques.

D.	The VFD shall be manufactured by Toshiba, Reliance Electric, Emerson Industrial Controls, Allen Bradley, or Westinghouse Electric Corporation or an approved equal.

2.02	VFD Supplied With A New Pump or Fan System

A.	The pump or fan manufacturer which supplies the VFD shall take "unit responsibility" for the complete pump or fan, motor, and VFD with all specified components.  The pump or fan will be specified in the Mechanical Section of the specifications and/or in the construction drawings which are included with this contract.  Unit responsibility shall include responsibility for interface and successful operation of all system components, including, but not limited to, hardware and electronics.  Pump or fan manufacturer is defined to mean the actual manufacturer of the variable speed pump or fan being submitted.

B.	The manufacturer of the VFD should also be the manufacturer of the motor.  If the VFD manufacturer does not manufacture motors, the VFD manufacturer shall submit a letter stating the motor furnished with the system is compatible with their VFD and that it will meet all the requirements of this specification.

C.	If a contractor provides a system other than that was specified on the construction drawings, the Contractor shall comply with the following:

1.	Meet the requirements of Section 2.02, A and B.

2.	Submit a harmonic study showing how the VFD meets the line noise limits as specified per Section 2.04 of this specification.  Sandia will provide the power system data required to perform the harmonic study.

2.03	VFD Supplied For An Existing Pump or Fan System

A.	The VFD manufacturer shall submit a letter stating that the use of their VFD is compatible with and properly sized for the existing pump or fan motor and that it will meet all the requirements of this specification.

B.	If the contractor provides a VFD other than what was called out on the construction drawings, the contractor shall submit the following:

1.	Submit a harmonic study showing how the substituted VFD meets the line noise limits as specified per Section 2.04 of this specification.  Sandia will provide the power system data required to perform the harmonic study.

2.04	VFD Maximum Voltage & Current Harmonic Distortion

A.	The harmonic voltage distortion shall not exceed the distortion limits at the point of common coupling (PCC) as recommended and defined by IEEE-519-1992 "Recommended Practices and Requirements for Harmonic Control in Electric Power Systems".  The harmonic voltage distortion shall be limited to 3% of fundamental for an individual frequency harmonic and a total harmonic voltage distortion (THVD) to 5% at the PCC without a major parallel resonance of the injected harmonic frequencies.  Existing harmonics shall be taken into account when preparing study.

B.	The harmonic current distortion shall not exceed the distortion limits at PCC as defined in IEEE-519-1992, Table 10.2.

2.05	Design Features

As a minimum, the VFD shall have the following design feature requirements:

A.	Automatic Restart:  The VFD shall be equipped such that upon restoration of input power the VFD will automatically restart and accelerate to the speed set by the remote speed reference signal.

B.	Speed Controls:

1.	The process follower shall be designed to accept a 3-15 psi pneumatic isolated speed reference signal, unless otherwise specified on the construction drawings.

2.	The VFD shall have an independent minimum frequency speed adjustment that is adjustable from 0-100% speed.

3.	The VFD shall have an independent maximum frequency speed adjustment that is adjustable from 0-100% speed.

4.	The VFD shall have a selectable V/Hz adjustment.

5.	The VFD shall have independent acceleration and deceleration adjustments that is adjustable over a minimum range of 2-120 seconds.

6.	The VFD shall have a minimum of three selectable output frequency ranges.

7.	The VFD, as a minimum, shall have two selectable stopping modes:  coast and ramp to stop.

8.	The VFD shall have bi-directional autospeed search for starting into rotating loads in both directions and for returning the motor to the desired speed in the proper rotational direction.

9.	Upon loss of the speed reference signal, the VFD shall operate at the preset minimum speed in order not to cause problems with the pump or fan system.

C.	The VFD should have an overload capability of 120% for 60 seconds and 110% continuous.  Refer to construction drawings for motor size.

D.	A D.C. bus discharge indicator shall be incorporated within the VFD control system.

E.	A heat sink over temperature protector should be incorporated within the VFD controller.

F.	The VFD shall contain separate terminal strips for input and output wire connections.

G.	The VFD controller shall contain the following door mounted switches:

1.	Hand-Off-Auto switch with the following features:

"Hand" - fan/pump enabled

"Off"  - fan/pump disabled

"Auto" - remote stop/start enabled

2.	A switch with the following functions:

Position 1 - Manual speed control

Position 2 - Auto speed control

H.	The VFD shall have a door-mounted output load ammeter, voltmeter, and speed indication.

I.	The VFD shall be supplied in a louvered NEMA 12, gasketed enclosure containing louvers with air filters, and fans as required for heat dissipation.

J.	The maximum acoustical noise levels for sound originating in VFD equipment shall not exceed 9 decibels above the room abient noise level where the VFD equipment will be located.  The room ambient noise level will be specified in the Mechanical Section of the contract specifications or drawings.

K.	The efficiency of the total VFD system shall be no less than 96.5% at full load when operating at full speed, and no less than 95% when operating at half speed.

L.	If electrical line noise filters or line reactors are required to meet the maximum allowable noise requirements per Section 2.04, they shall be as recommended by the VFD manufacturer.

M.	The VFD shall be capable of power loss ride through to prevent shutdown during power losses for a minimum of three cycles.

An input power disconnect switch shall provide a positive disconnecting means between the controller and all phases of the incoming AC line.  This disconnect shall mount inside the controller enclosure and include a mounting bracket and through-the-door interlocking handle with provisions for padlocking.  The switch shall be a thermal magnetic, molded case circuit breaker.  The circuit breaker shall be sized to interrupt 25,000 amperes (symmetrical) fault current unless otherwise noted.

N.	Manual Bypass.  A manual bypass shall be provided, unless otherwise specified in drawings; the manual bypass should be accomplished using magnetic contactors.  No IEC type contactors will be allowed.  All the circuitry necessary to safely transfer the motor from the VFD to the power line, or from the power line to the VFD while the motor is at zero speed, should be included.  Two motor contactors, electrically interlocked, shall be utilized.  One contactor is connected between the controller output and the motor and is controlled by the controller regulator.  The second contactor is connected between the bypass power line and the motor, providing across-the-line starting.  Motor protection shall be provided in both the "controller" mode and the "bypass" mode by a motor overload relay.  The relay control logic shall be 115 VAC. Common start-stop commands in the "controller" mode and the "bypass" mode shall also be included within this enclosure.  The bypass circuit is to include a door interlocked, main power input disconnect circuit breaker that provides positive shutdown of all input power to both the bypass circuitry and the VFD.  The bypass circuit shall include a second-door interlocked input disconnect circuit breaker installed in the VFD.  This disconnect shall provide the ability to safely troubleshoot and test the controller, both energized and de-energized, while operating in the "bypass" mode.  All of this equipment shall be mounted within the controller enclosure.

2.06	Protective Features

A.	The VFD shall be designed to be self protecting from electrical  damage due to normal transients and surges in the incoming power line, grounding or disconnection of its output power, and any interruption in or run away of the incoming speed reference signal.  Protection is defined as a normal shutdown with no component damage.  The available fault current at the VFD will be 25,000 amperes, unless otherwise noted.

B.	As a minimum, the VFD shall have the following protective features:

1.	Ground fault protection.

2.	Short circuit protection.

3.	Overload protection of VFD unit.

4.	Separate motor overload relay with reset button extending through door.

5.	A minimum current limit adjustable (output of drive) from 60-100%.

6.	Current limited stall prevention.

7.	Current limiting D.C. bus fuse.

8.	D.C. bus under voltage.

9.	D.C. bus over voltage.

10.	Loss of input phase protection.

11.	Over frequency protection.

12.	Over temperature protection.

2.07	Diagnostic Fault Indicators

A.	The VFD shall have a self-diagnostic check for fault conditions.  Faults shall be displayed on the front panel.

B.	As a minimum, the following faults shall be displayed:

1.	Overcurrent.

2.	Short circuit.

3.	Ground fault.

4.	Overload.

5.	Overvoltage.

6.	Undervoltage.

7.	Overtemperature.

8.	Control function error.

2.08	VFD Environmental and Service Conditions

The VFD shall be designed to operate within the following environmental or service conditions:

A.	Ambient service temperature:  0oC to 40oC.

B.	Humidity:  non-condensing to 90%.

C.	Altitude:  5,500 feet (1,676 m).

D.	Input Voltage:	The input voltage will be specified on the construction drawings and will either be 200 VAC + 10% or 460 VAC + 10%.

E.	Input Frequency:	60 Hertz + 2%.

2.09	Spare Parts

Unless otherwise specified, the Contractor shall provide spare parts as recommended by the VFD manufacturer.  As a minimum, the spare parts should include the following:

A.	One spare for each type of printed circuit card.

B.	One set of fuses for each fuse size.

C.	One power transistor for each transistor rating supplied.

2.10	VFD Motor Requirements

A.	New pump or fan motors operated from a VFD system shall meet the following requirements:

1.	Shall conform to the latest applicable requirements of NEMA, IEEE, ANSI, and NEC standards.

2.	Shall be designed for continuous duty operation, NEMA Design B.

3.	Shall have a service factor of 1.15.

4.	Shall be furnished with Class F insulation.

5.	Shall be energy efficient and meet NEMA S484E efficiency standard.

B.	For existing pump or fan motors to be operated from a VFD system;  Sandia will provide nameplate information on an attached sheet or it will be shown on the construction drawings.  See Section 2.03 for VFD manufacturer's requirements.

PART 3 - EXECUTION

3.01	EXAMINATION

The Contractor shall examine areas and conditions under which the VFD system is to be installed and notify the SDR in writing of those conditions detrimental to proper completion of the work.  Work shall not proceed until unsatisfactory conditions have been corrected in a manner acceptable to the SDR.

3.02	PREPARATION

The Contractor shall provide indoor storage for the VFD to meet service conditions in Section 2.08 A and B.

3.03	INSTALLATION

A.	Construction work shall be performed in a thorough and conscientious manner in accordance with the specifications, construction drawings, and the requirements of the referenced codes and standards of Section 1.02.

B.	Installation of the VFD and accessory items shall be made in accordance with the manufacturer's written installation instructions and per SNL's standard specification 16001 - Electrical Work.

3.04	Field QUALITY CONTROL

A.	The Contractor shall arrange and pay for the services of the VFD manufacturers' service engineer to test, checkout, and start up the VFD system.

B.	Under no circumstances are any portions of the VFD system to be energized without authorization from the VFD manufacturer's representative.

C.	The Contractor shall demonstrate trouble free, stable operation for conditions of starting, full load, three-quarter load, half load, one-quarter load, no load, and intermediate loads.

D.	Tests shall include 100 hours of operation under load to demonstrate adequacy of equipment under thermal and voltage stresses, and that harmonic and other interferences do not adversely affect the electrical instrumentation and communication system.

E.	Sandia will test the VFD at the point of common coupling, at no charge to the Contractor, before and after it is installed with a Dranetz Model 658 power analyzer.  The power analyzer is capable of measuring total harmonic voltage and current distortion.  If the harmonic voltage and current distortion limits, as defined in section 2.04 of this specification, are exceeded, the Contractor agrees to furnish and install, at no cost to Sandia, any devices necessary to reduce the distortion to acceptable limits.

F.	The VFD manufacturer's service engineer shall prepare final written documents of installation and inspection tests made in the field, complete with meter readings and recordings, where applicable, and these documents shall be submitted to the SDR for approval.

G.	Test Reports:  VFD supplier shall furnish copies of each test report as required by this specification.

END OF SECTION