## 25F nomo
Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 044
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6678.628
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 580.04 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2532.5 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1350 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2926.32 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2532.5 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3237.46 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 876.89 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3553.53 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 1640.98 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3664.65 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 775 | 2926.32 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1350 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1266.52 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1640.98 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1968.65 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1968.65 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3237.46 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 2585.5 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1884.34 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3655.53 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1000 | 460 | 2585.5 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 580.04 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3553.53 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 876.89 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2492.95 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1266.52 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 3655.53 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G10 | 1000 | 140 | 1884.34 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3664.65 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G13 | 1400 | 140 | 2492.95 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 044
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6352.4447
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1199.05 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2591.47 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1848.32 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2916.66 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2591.47 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3175.54 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 1473.25 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3486.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2136.35 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3580.93 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 775 | 2916.66 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1848.32 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1796.36 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2136.35 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2519.59 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2519.59 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3175.54 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3461.58 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 2474.61 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3593.29 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1000 | 460 | 3461.58 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1199.05 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3486.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1473.25 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 3056.15 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1796.36 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 3593.29 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G10 | 1000 | 140 | 2474.61 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3580.93 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G13 | 1400 | 140 | 3056.15 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 044
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6072.0087
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1631.9 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2534.97 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2680.54 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2881.65 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2534.97 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3064.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 1950.44 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3392.21 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2857.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 3154.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2881.65 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2680.54 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2272.14 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2857.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3051.43 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3051.43 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3064.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3357.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3316.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 3293.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3357.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1631.9 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3392.21 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1950.44 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 3404.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2272.14 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 3293.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3316.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 3154.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 3404.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 044
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4973.606
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2438.8 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2505.4 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2466.26 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2618.14 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2505.4 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2823.13 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2553.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3142.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2584.88 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1913.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2618.14 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2466.26 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2759.98 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2584.88 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2795.25 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2795.25 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2823.13 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3117.77 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3084.92 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 2078.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3117.77 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2438.8 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3142.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2553.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 2223.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2759.98 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 2078.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3084.92 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1913.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2223.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 044
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4631.9447
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2370.21 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2426.65 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2386.15 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2480.05 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2426.65 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2702.74 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2409.49 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3047.19 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2445.63 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1662.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2480.05 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2386.15 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2629.68 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2445.63 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2663.58 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2663.58 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2702.74 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3008.47 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 2974.58 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1800.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3008.47 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2370.21 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3047.19 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2409.49 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 1954.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2629.68 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1800.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2974.58 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1662.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1954.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
G0 | 580.04 | 1199.05 | 1631.9 | 2438.8 | 2370.21
G1 | 1350 | 1848.32 | 2680.54 | 2466.26 | 2386.15 | Season/Year: | WINTER 2009
G2 | 2532.5 | 2591.47 | 2534.97 | 2505.4 | 2426.65 | Direction: | South-to-North (SN)
G3 | 876.89 | 1473.25 | 1950.44 | 2553.24 | 2409.49 | Case Loads: | Heavy Loads
G4 | 1640.98 | 2136.35 | 2857.37 | 2584.88 | 2445.63 | Outage: | 044
G5 | 2926.32 | 2916.66 | 2881.65 | 2618.14 | 2480.05 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 1266.52 | 1796.36 | 2272.14 | 2759.98 | 2629.68 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 1968.65 | 2519.59 | 3051.43 | 2795.25 | 2663.58 | Study Person: | FRP9899
G8 | 3237.46 | 3175.54 | 3064.61 | 2823.13 | 2702.74 | Source: | 044WINTER09v2SNH(SN@100MW)
G9 | 1884.34 | 2474.61 | 3316.03 | 3084.92 | 2974.58
G10 | 2585.5 | 3461.58 | 3357.03 | 3117.77 | 3008.47
G11 | 3553.53 | 3486.91 | 3392.21 | 3142.2 | 3047.19
G12 | 2492.95 | 3056.15 | 3404.47 | 2223.32 | 1954.86
G13 | 3655.53 | 3593.29 | 3293.36 | 2078.68 | 1800.14
G14 | 3664.65 | 3580.93 | 3154.89 | 1913.3 | 1662.69
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 044 | Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6678.628 | 580.04 | 1350 | 2532.5 | 876.89 | 1640.98 | 2926.32 | 1266.52 | 1968.65 | 3237.46 | 1884.34 | 2585.5 | 3553.53 | 2492.95 | 3655.53 | 3664.65
35F | 6352.4447 | 1199.05 | 1848.32 | 2591.47 | 1473.25 | 2136.35 | 2916.66 | 1796.36 | 2519.59 | 3175.54 | 2474.61 | 3461.58 | 3486.91 | 3056.15 | 3593.29 | 3580.93
45F | 6072.0087 | 1631.9 | 2680.54 | 2534.97 | 1950.44 | 2857.37 | 2881.65 | 2272.14 | 3051.43 | 3064.61 | 3316.03 | 3357.03 | 3392.21 | 3404.47 | 3293.36 | 3154.89
60F | 4973.606 | 2438.8 | 2466.26 | 2505.4 | 2553.24 | 2584.88 | 2618.14 | 2759.98 | 2795.25 | 2823.13 | 3084.92 | 3117.77 | 3142.2 | 2223.32 | 2078.68 | 1913.3
70F | 4631.9447 | 2370.21 | 2386.15 | 2426.65 | 2409.49 | 2445.63 | 2480.05 | 2629.68 | 2663.58 | 2702.74 | 2974.58 | 3008.47 | 3047.19 | 1954.86 | 1800.14 | 1662.69

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 579.73 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 511.54 | 511.61 | 6678.23 | 580.04 | -923.56 | FULL
G1 | 2104.64 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.7 | 534.14 | 534.08 | 6654.55 | 1350 | -1712.89 | CTG_FAIL_IN_FULL
G2 | 2533.56 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -9.06 | -506.6 | -506.74 | 6684.09 | 2532.5 | -1878.61 | FULL
G3 | 876.7 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 517.64 | 517.69 | 6680.67 | 876.89 | -1019.13 | FULL
G4 | 1641.04 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 515.06 | 515.92 | 6634.54 | 1640.98 | -1377.99 | FULL
G5 | 2928.85 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -9.06 | -525.79 | -525.67 | 6696.18 | 2926.32 | -2027.42 | FULL
G6 | 1266.57 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 518.24 | 518.19 | 6685.4 | 1266.52 | -1110.83 | FULL
G7 | 1968.85 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 506.64 | 505.65 | 6639.86 | 1968.65 | -1436.71 | FULL
G8 | 3238.94 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -64.91 | -2704.34 | -2706.19 | 6698.34 | 3237.46 | -2076.41 | CTG_FAIL_IN_FULL
G9 | 1884.61 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 516.37 | 517.43 | 6698.05 | 1884.34 | -1248.88 | FULL
G10 | 2585.9 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 512.14 | 512.19 | 6653.51 | 2585.5 | -1562.89 | FULL
G11 | 3551.7 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -64.91 | -2702.11 | -2702.45 | 6694.1 | 3553.53 | -2036.41 | CTG_FAIL_IN_FULL
G12 | 2493.92 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 507.32 | 507.39 | 6713.74 | 2492.95 | -1415.91 | FULL
G13 | 3656.11 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3617.4 | 3617.1 | 6679.6 | 3655.53 | -1988.47 | FULL
G14 | 3663.09 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3624.8 | 3622.11 | 6688.56 | 3664.65 | -1930 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1198.87 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 502.92 | 502.85 | 6360.04 | 1199.05 | -1201.31 | FULL
G1 | 1848.46 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 497.87 | 497.81 | 6314.25 | 1848.32 | -1500.79 | FULL
G2 | 2591.7 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -9.06 | -494.2 | -494 | 6347.89 | 2591.47 | -1839.68 | FULL
G3 | 1473.28 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 503.47 | 503.55 | 6364.38 | 1473.25 | -1286.27 | FULL
G4 | 2135.11 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 492.36 | 492.42 | 6321.1 | 2136.35 | -1588.94 | FULL
G5 | 2916.26 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -9.06 | -493.71 | -493.56 | 6357.64 | 2916.66 | -1954.45 | FULL
G6 | 1796.54 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 502.88 | 502.92 | 6368.03 | 1796.36 | -1345.43 | FULL
G7 | 2519.98 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 498.09 | 498.04 | 6326.59 | 2519.59 | -1677.76 | FULL
G8 | 3176.04 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -64.91 | -2625.65 | -2625.66 | 6356.37 | 3175.54 | -1979.96 | CTG_FAIL_IN_FULL
G9 | 2473.23 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 501.92 | 501.98 | 6384.93 | 2474.61 | -1504.53 | FULL
G10 | 3462.53 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -64.91 | -2632.97 | -2633.11 | 6343.36 | 3461.58 | -1988.68 | CTG_FAIL_IN_FULL
G11 | 3487.53 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -64.91 | -2625.97 | -2625.99 | 6351.68 | 3486.91 | -1926.51 | CTG_FAIL_IN_FULL
G12 | 3057.25 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 499.97 | 499.89 | 6401.32 | 3056.15 | -1666.73 | FULL
G13 | 3594.09 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3558.94 | 3561.04 | 6339.78 | 3593.29 | -1895.38 | FULL
G14 | 3581.19 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3546.5 | 3548.32 | 6349.31 | 3580.93 | -1824.37 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1632.19 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 481.9 | 481.86 | 6090.95 | 1631.9 | -1420.69 | FULL
G1 | 2679.37 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -9.06 | -486.34 | -486.41 | 6058.02 | 2680.54 | -1930.47 | FULL
G2 | 2535.26 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -9.06 | -480.54 | -480.43 | 6058.27 | 2534.97 | -1772 | FULL
G3 | 1950.72 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 490.95 | 490.76 | 6096.24 | 1950.44 | -1525.95 | FULL
G4 | 2857.88 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -64.91 | -2543.59 | -2543.48 | 6057.32 | 2857.37 | -1958.7 | CTG_FAIL_IN_FULL
G5 | 2881.99 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -64.91 | -2542.39 | -2542.4 | 6067.32 | 2881.65 | -1908.77 | CTG_FAIL_IN_FULL
G6 | 2272.13 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 2.71 | 489.94 | 490.75 | 6100.79 | 2272.14 | -1579.75 | FULL
G7 | 3051.89 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -64.91 | -2549.5 | -2549.43 | 6053.73 | 3051.43 | -1943.92 | CTG_FAIL_IN_FULL
G8 | 3065.05 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -64.91 | -2536.15 | -2536.06 | 6063.75 | 3064.61 | -1870.52 | CTG_FAIL_IN_FULL
G9 | 3316.55 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -64.91 | -2532.71 | -2532.73 | 6123.82 | 3316.03 | -1934.95 | CTG_FAIL_IN_FULL
G10 | 3357.54 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -64.91 | -2542.13 | -2542.18 | 6051.3 | 3357.03 | -1899.7 | CTG_FAIL_IN_FULL
G11 | 3392.75 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -64.91 | -2543.52 | -2543.53 | 6061.4 | 3392.21 | -1838.56 | CTG_FAIL_IN_FULL
G12 | 3404.98 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.03 | -439.16 | -439.02 | 6117.55 | 3404.47 | -1821.45 | FULL
G13 | 3293.9 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.03 | -435.02 | -434.98 | 6038.83 | 3293.36 | -1676.36 | FULL
G14 | 3156.1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.03 | -431.83 | -431.83 | 6040.84 | 3154.89 | -1531.18 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2439.15 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2223.03 | -2221.43 | 5026.44 | 2438.8 | -1676.53 | FULL
G1 | 2466.56 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2217.18 | -2215.47 | 4955.31 | 2466.26 | -1606.93 | FULL
G2 | 2506.51 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2230.25 | -2228.71 | 4966.03 | 2505.4 | -1558.49 | FULL
G3 | 2553.55 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2223.05 | -2222.13 | 5024.95 | 2553.24 | -1657.09 | FULL
G4 | 2584.98 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2231.83 | -2230.62 | 4953.8 | 2584.88 | -1603.45 | FULL
G5 | 2618.49 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2234.47 | -2236.15 | 4965.33 | 2618.14 | -1555.12 | FULL
G6 | 2760.33 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2239.21 | -2240.15 | 5022.87 | 2759.98 | -1646.45 | FULL
G7 | 2795.66 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2246.33 | -2247.01 | 4952.93 | 2795.25 | -1598.75 | FULL
G8 | 2823.52 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2248.56 | -2249.24 | 4964.73 | 2823.13 | -1546.19 | FULL
G9 | 3085.35 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2242.65 | -2243.3 | 5025.04 | 3084.92 | -1612.86 | FULL
G10 | 3118.31 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2247.88 | -2245.97 | 4954.89 | 3117.77 | -1562.8 | FULL
G11 | 3142.76 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2247.39 | -2247.99 | 4966.86 | 3142.2 | -1508.37 | FULL
G12 | 2223.69 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.03 | -426.92 | -426.97 | 4987.32 | 2223.32 | -969.55 | FULL
G13 | 2078.79 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.03 | -425.54 | -425.5 | 4913.79 | 2078.68 | -816.02 | FULL
G14 | 1915.95 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.03 | -421.54 | -421.67 | 4923.8 | 1913.3 | -651.83 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2370.47 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2148.53 | -2149.21 | 4683.83 | 2370.21 | -1567.73 | FULL
G1 | 2386.4 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | -66.85 | -2108.66 | -2107.6 | 4613.36 | 2386.15 | -1506.03 | FULL
G2 | 2426.91 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.28 | -2153.15 | -2154.25 | 4625.93 | 2426.65 | -1460.97 | FULL
G3 | 2411.83 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.86 | -2135 | -2133.74 | 4680.55 | 2409.49 | -1521.41 | FULL
G4 | 2448.28 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.86 | -2140.14 | -2139.04 | 4610.74 | 2445.63 | -1470.75 | FULL
G5 | 2480.43 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.86 | -2143.18 | -2141.56 | 4623.47 | 2480.05 | -1421.62 | FULL
G6 | 2632.25 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.86 | -2146.55 | -2147.77 | 4679.81 | 2629.68 | -1518.66 | FULL
G7 | 2665.41 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.86 | -2150.88 | -2152.68 | 4610.25 | 2663.58 | -1467.81 | FULL
G8 | 2704.63 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.86 | -2155.67 | -2157.37 | 4622.83 | 2702.74 | -1420.66 | FULL
G9 | 2974.17 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.86 | -2147.13 | -2148.36 | 4682.77 | 2974.58 | -1495.57 | FULL
G10 | 3009.69 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.86 | -2152.02 | -2153.25 | 4613.05 | 3008.47 | -1443.87 | FULL
G11 | 3049.82 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.86 | -2167.78 | -2169.52 | 4625.54 | 3047.19 | -1397.18 | FULL
G12 | 1957.29 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.03 | -421.92 | -421.85 | 4646.02 | 1954.86 | -758.77 | FULL
G13 | 1800.19 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.03 | -420.17 | -420.08 | 4574.52 | 1800.14 | -601.67 | FULL
G14 | 1662.65 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -9.03 | -421.06 | -420.99 | 4586.5 | 1662.69 | -459.92 | FULL
044WINTER09v2SNH(SN@100MW)