## 25F nomo
Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 014
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6645.72
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 344.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 569.48 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 517.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1574.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 569.48 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3331.86 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 140 | 1350.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2683.57 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1462.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2221.3 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1574.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 517.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3109.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1462.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3230.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3230.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3331.86 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3191.85 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3183.17 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2945.74 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 460 | 3191.85 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 344.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2683.57 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1350.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 3037 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3109.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2945.74 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3183.17 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2221.3 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 3037 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 014
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6320.1133
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 709.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 934.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 826.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1925.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 934.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3514.89 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1663.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3064.34 | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1781.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2548.14 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1925.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 826.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3368.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1781.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3506.12 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3506.12 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3514.89 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3098.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3090.11 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2963.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3098.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 709.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3064.34 | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1663.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2948.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3368.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2963.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3090.11 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2548.14 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2948.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 014
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6034.3573
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 453.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 672.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 566.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1604.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 672.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3299.26 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1404.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3059.19 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1492.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2615.42 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 1604.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 566.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3127.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1492.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3247.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3247.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3299.26 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3045.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3037.52 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2905.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3045.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 453.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3059.19 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1404.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2888.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3127.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2905.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3037.52 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2615.42 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2888.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 014
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4968.7253
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1813.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2039.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1926.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2852.49 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2039.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3079.08 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2639.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2507.75 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2748.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1952.06 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2852.49 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1926.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3235.81 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2748.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3248.23 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3248.23 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3079.08 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2834.91 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2823.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2608.73 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2834.91 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1813.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2507.75 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2639.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2660.7 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3235.81 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2608.73 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2823.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1952.06 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2660.7 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 014
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4626.076
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2064.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2269.49 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2171.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2486.2 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
100 | 775 | 2269.49 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2240.59 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2864.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1633.66 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2996.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1111.56 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2486.2 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2171.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3167.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2996.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2841.56 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2841.56 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
525 | 775 | 2240.59 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2225.49 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2741.13 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1717.91 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2225.49 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2064.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1633.66 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2864.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2353.15 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3167.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1717.91 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2741.13 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1111.56 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2353.15 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
G0 | 344.75 | 709.21 | 453.08 | 1813.12 | 2064.91
G1 | 517.86 | 826.24 | 566.54 | 1926.88 | 2171.23 | Season/Year: | WINTER 2009
G2 | 569.48 | 934.96 | 672.87 | 2039.04 | 2269.49 | Direction: | North-to-South (NS)
G3 | 1350.61 | 1663.84 | 1404.7 | 2639.25 | 2864.09 | Case Loads: | Heavy Loads
G4 | 1462.77 | 1781.82 | 1492.9 | 2748.64 | 2996.87 | Outage: | 014
G5 | 1574.86 | 1925.17 | 1604.2 | 2852.49 | 2486.2 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3109.63 | 3368.58 | 3127.34 | 3235.81 | 3167.26 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3230.81 | 3506.12 | 3247.73 | 3248.23 | 2841.56 | Study Person: | FRP9899
G8 | 3331.86 | 3514.89 | 3299.26 | 3079.08 | 2240.59 | Source: | 014WINTER09v2NSH
G9 | 3183.17 | 3090.11 | 3037.52 | 2823.28 | 2741.13
G10 | 3191.85 | 3098.5 | 3045.25 | 2834.91 | 2225.49
G11 | 2683.57 | 3064.34 | 3059.19 | 2507.75 | 1633.66
G12 | 3037 | 2948.01 | 2888.97 | 2660.7 | 2353.15
G13 | 2945.74 | 2963.35 | 2905.68 | 2608.73 | 1717.91
G14 | 2221.3 | 2548.14 | 2615.42 | 1952.06 | 1111.56
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 014 | Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6645.72 | 344.75 | 517.86 | 569.48 | 1350.61 | 1462.77 | 1574.86 | 3109.63 | 3230.81 | 3331.86 | 3183.17 | 3191.85 | 2683.57 | 3037 | 2945.74 | 2221.3
35F | 6320.1133 | 709.21 | 826.24 | 934.96 | 1663.84 | 1781.82 | 1925.17 | 3368.58 | 3506.12 | 3514.89 | 3090.11 | 3098.5 | 3064.34 | 2948.01 | 2963.35 | 2548.14
45F | 6034.3573 | 453.08 | 566.54 | 672.87 | 1404.7 | 1492.9 | 1604.2 | 3127.34 | 3247.73 | 3299.26 | 3037.52 | 3045.25 | 3059.19 | 2888.97 | 2905.68 | 2615.42
60F | 4968.7253 | 1813.12 | 1926.88 | 2039.04 | 2639.25 | 2748.64 | 2852.49 | 3235.81 | 3248.23 | 3079.08 | 2823.28 | 2834.91 | 2507.75 | 2660.7 | 2608.73 | 1952.06
70F | 4626.076 | 2064.91 | 2171.23 | 2269.49 | 2864.09 | 2996.87 | 2486.2 | 3167.26 | 2841.56 | 2240.59 | 2741.13 | 2225.49 | 1633.66 | 2353.15 | 1717.91 | 1111.56

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 342.42 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 473.16 | 473.22 | 6654.11 | 344.75 | 9.1 | FULL
G1 | 517.47 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 476.01 | 475.83 | 6582.65 | 517.86 | 148.03 | FULL
G2 | 568.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 474.05 | 473.97 | 6594.14 | 569.48 | 204.07 | FULL
G3 | 1352.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 484.48 | 484.35 | 6649.96 | 1350.61 | 640.52 | FULL
G4 | 1465.28 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 484.87 | 484.81 | 6582.14 | 1462.77 | 736.15 | FULL
G5 | 1578.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 485.46 | 485.38 | 6595.99 | 1574.86 | 831.73 | FULL
G6 | 3122.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 492.24 | 492.16 | 6692.89 | 3109.63 | 1747.87 | FULL
G7 | 3247.19 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 490.83 | 491 | 6630.58 | 3230.81 | 1845.75 | FULL
G8 | 3349.36 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.88 | 459.37 | 459.45 | 6649.08 | 3331.86 | 1933.35 | FULL
G9 | 3198.97 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -511.02 | -510.37 | 6720.12 | 3183.17 | 1981.38 | FULL
G10 | 3208.74 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -510.99 | -510.32 | 6654.5 | 3191.85 | 2017.31 | FULL
G11 | 2692.38 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.88 | 458.73 | 458.81 | 6645.27 | 2683.57 | 1773.27 | FULL
G12 | 3052.6 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -515.62 | -515.01 | 6730.48 | 3037 | 2048.24 | FULL
G13 | 2959.41 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.88 | 459.14 | 459.22 | 6658.87 | 2945.74 | 2032.92 | FULL
G14 | 2227.28 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.88 | 459.24 | 459.3 | 6645.02 | 2221.3 | 1672.59 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 707.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 469.35 | 469.14 | 6318.18 | 709.21 | 256.02 | FULL
G1 | 826.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 469.79 | 469.58 | 6248.41 | 826.24 | 356.06 | FULL
G2 | 936.73 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 469.96 | 469.75 | 6261.04 | 934.96 | 450.36 | FULL
G3 | 1666.6 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 478.21 | 478.12 | 6320.56 | 1663.84 | 853.75 | FULL
G4 | 1785.19 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 478.56 | 478.69 | 6254.09 | 1781.82 | 953.02 | FULL
G5 | 1930.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 480.08 | 480.19 | 6270.91 | 1925.17 | 1065.86 | FULL
G6 | 3386.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 480.18 | 480.42 | 6374.27 | 3368.58 | 1921.09 | FULL
G7 | 3526.55 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -489.56 | -489.34 | 6313.44 | 3506.12 | 2040.21 | FULL
G8 | 3535.41 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -489.41 | -489.13 | 6329.86 | 3514.89 | 2075.97 | FULL
G9 | 3104.75 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -501.74 | -500.99 | 6387.46 | 3090.11 | 1955.79 | FULL
G10 | 3113.32 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -500.36 | -499.61 | 6322.32 | 3098.5 | 1992.72 | FULL
G11 | 3077.96 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | 2.88 | 459.82 | 459.8 | 6334.11 | 3064.34 | 2012.44 | FULL
G12 | 2961.76 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -501.24 | -500.87 | 6400.58 | 2948.01 | 2026.75 | FULL
G13 | 2976.29 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -502.97 | -502.64 | 6335.72 | 2963.35 | 2067.04 | FULL
G14 | 2558.53 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.88 | 459.76 | 459.84 | 6330.75 | 2548.14 | 1887.61 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 451.95 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 435.09 | 434.99 | 6034.27 | 453.08 | 126.93 | FULL
G1 | 565.9 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 435.32 | 435.22 | 5964.33 | 566.54 | 225.13 | FULL
G2 | 673.61 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 435.43 | 435.37 | 5976.68 | 672.87 | 318.22 | FULL
G3 | 1408.38 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 443.6 | 443.71 | 6034.73 | 1404.7 | 723.95 | FULL
G4 | 1495.33 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 442.71 | 442.8 | 5967.28 | 1492.9 | 806.96 | FULL
G5 | 1607.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 443.26 | 443.39 | 5982.65 | 1604.2 | 901.76 | FULL
G6 | 3143.3 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 446.96 | 447.09 | 6081.51 | 3127.34 | 1803.11 | FULL
G7 | 3264.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 446.71 | 446.85 | 6020.1 | 3247.73 | 1907.47 | FULL
G8 | 3316.2 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 445.87 | 445.8 | 6039.24 | 3299.26 | 1965.83 | FULL
G9 | 3051.29 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -493.53 | -492.9 | 6103.15 | 3037.52 | 1955.37 | FULL
G10 | 3059.21 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -492.35 | -491.96 | 6038.08 | 3045.25 | 1991.09 | FULL
G11 | 3074.14 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -491.26 | -490.87 | 6052.03 | 3059.19 | 2030.57 | FULL
G12 | 2901.96 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -492.87 | -491.72 | 6116.33 | 2888.97 | 2010 | FULL
G13 | 2918.67 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -493.21 | -492.52 | 6051.55 | 2905.68 | 2073.24 | FULL
G14 | 2625.7 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -201.02 | -200.99 | 6053.43 | 2615.42 | 1930.85 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1817.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 443.46 | 443.55 | 4962.66 | 1813.12 | 1021.99 | FULL
G1 | 1932.29 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 443.73 | 443.83 | 4898.61 | 1926.88 | 1117.7 | FULL
G2 | 2044.68 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 444.5 | 444.61 | 4916.8 | 2039.04 | 1210.53 | FULL
G3 | 2649.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 447.72 | 447.76 | 4985.35 | 2639.25 | 1533.82 | FULL
G4 | 2760.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 447.66 | 447.69 | 4923.73 | 2748.64 | 1611.72 | FULL
G5 | 2864.52 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 447.66 | 447.83 | 4943.89 | 2852.49 | 1710 | FULL
G6 | 3252.75 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -471.63 | -472.05 | 5021.03 | 3235.81 | 1963.72 | FULL
G7 | 3265.03 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -469.74 | -470.2 | 4956.64 | 3248.23 | 2016.95 | FULL
G8 | 3095.26 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -191.42 | -191.41 | 4967.88 | 3079.08 | 1944.33 | FULL
G9 | 2835.46 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -476.13 | -475.35 | 5028.66 | 2823.28 | 1938.92 | FULL
G10 | 2846.9 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -475.93 | -475.07 | 4964.49 | 2834.91 | 1992.89 | FULL
G11 | 2517.48 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -190.23 | -190.23 | 4969.68 | 2507.75 | 1835.55 | FULL
G12 | 2672.08 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -12.83 | -457.03 | -457 | 5043.92 | 2660.7 | 2021.24 | FULL
G13 | 2619.49 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -191.4 | -191.4 | 4979 | 2608.73 | 2001.95 | FULL
G14 | 1958.09 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -191 | -190.99 | 4968.54 | 1952.06 | 1680.02 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2071.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 444.9 | 444.84 | 4634.52 | 2064.91 | 1194.03 | FULL
G1 | 2180.87 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 445.86 | 444.57 | 4571.31 | 2171.23 | 1285.1 | FULL
G2 | 2278.54 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 444.82 | 444.95 | 4590.17 | 2269.49 | 1359.5 | FULL
G3 | 2875.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 447.41 | 447.45 | 4660.17 | 2864.09 | 1685.42 | FULL
G4 | 3011.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 448.52 | 447.76 | 4601.29 | 2996.87 | 1785.81 | FULL
G5 | 2497.09 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -172.3 | -172.29 | 4603.32 | 2486.2 | 1531.01 | FULL
G6 | 3184.42 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -460.6 | -459.63 | 4686.57 | 3167.26 | 1969.98 | FULL
G7 | 2853.95 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -173.43 | -173.42 | 4608.61 | 2841.56 | 1825.21 | FULL
G8 | 2248.6 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -174.39 | -174.37 | 4603.41 | 2240.59 | 1527.62 | FULL
G9 | 2752.54 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -462.25 | -461.4 | 4694.09 | 2741.13 | 1927.55 | FULL
G10 | 2233.89 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -173.22 | -173.21 | 4609.47 | 2225.49 | 1679.62 | FULL
G11 | 1637.56 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -173.74 | -173.73 | 4606.54 | 1633.66 | 1385.23 | FULL
G12 | 2361.92 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -172.13 | -172.12 | 4700.91 | 2353.15 | 1864.73 | FULL
G13 | 1722.63 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -173.33 | -173.31 | 4611.42 | 1717.91 | 1549.58 | FULL
G14 | 1112.87 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.44 | -173.99 | -173.98 | 4609.34 | 1111.56 | 1246.84 | FULL
014WINTER09v2NSH