## 25F nomo
Sammamish-Novelty Hill #2 230kV Line (PSE) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 037
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6645.2193
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 385.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 570.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 473.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1563.31 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 570.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3021.95 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1356.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2877.33 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1470.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2774.1 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1563.31 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 473.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2785.25 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1470.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2974.85 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2974.85 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3021.95 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2783.21 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2486.55 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2560.01 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2783.21 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 385.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2877.33 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1356.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2452.79 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2785.25 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2560.01 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2486.55 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 2774.1 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2452.79 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Sammamish-Novelty Hill #2 230kV Line (PSE) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 037
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6315.81
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 793.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 941.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 834.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1921.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 941.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3034.78 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1644.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2944.37 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1781.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2745.59 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1921.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 834.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2786.56 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1781.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2947.14 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2947.14 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3034.78 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2777.83 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2593.67 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2602.35 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2777.83 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 793.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2944.37 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1644.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2514.21 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2786.56 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2602.35 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2593.67 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 2745.59 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2514.21 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Sammamish-Novelty Hill #2 230kV Line (PSE) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 037
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6031.17
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 488.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 664.18 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 553.66 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1571.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 664.18 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3100.76 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1373.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2902.33 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1475.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2682.8 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1571.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 553.66 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2723.57 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1475.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2909.81 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2909.81 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3100.76 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2709.53 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2458.25 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2648.85 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 2709.53 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 488.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2902.33 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1373.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2449.54 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2723.57 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2648.85 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2458.25 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2682.8 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2449.54 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Sammamish-Novelty Hill #2 230kV Line (PSE) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 037
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4970.78
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1815.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2028.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1916.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2837.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2028.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3177.43 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2627.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2849.05 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2730.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2323.67 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2837.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1916.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2821.32 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2730.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3001.47 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3001.47 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3177.43 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2823.31 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 2644.74 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2692.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2823.31 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1815.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2849.05 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2627.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2568.88 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2821.32 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 2692.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2644.74 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2323.67 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2568.88 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Sammamish-Novelty Hill #2 230kV Line (PSE) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 037
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4632.6447
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2069.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2268.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2141.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2899.84 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
100 | 775 | 2268.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2585.84 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2858.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1979.38 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2963.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1459.23 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2899.84 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2141.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2823.19 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2963.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2996.66 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2996.66 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2585.84 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2588.21 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2630.03 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2068.93 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2588.21 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2069.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1979.38 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2858.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2545.83 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2823.19 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2068.93 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2630.03 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1459.23 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2545.83 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Sammamish-Novelty Hill #2 230kV Line (PSE) (COV-CRES BYP @ COV)
G0 | 385.91 | 793.85 | 488.41 | 1815.17 | 2069.86
G1 | 473.8 | 834.28 | 553.66 | 1916.02 | 2141.14 | Season/Year: | WINTER 2009
G2 | 570.9 | 941.23 | 664.18 | 2028.9 | 2268.68 | Direction: | North-to-South (NS)
G3 | 1356.1 | 1644.85 | 1373.87 | 2627.93 | 2858.45 | Case Loads: | Heavy Loads
G4 | 1470.47 | 1781.58 | 1475.99 | 2730.05 | 2963.82 | Outage: | 037
G5 | 1563.31 | 1921.28 | 1571.25 | 2837.17 | 2899.84 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2785.25 | 2786.56 | 2723.57 | 2821.32 | 2823.19 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2974.85 | 2947.14 | 2909.81 | 3001.47 | 2996.66 | Study Person: | FRP9899
G8 | 3021.95 | 3034.78 | 3100.76 | 3177.43 | 2585.84 | Source: | 037WINTER09v2NSH
G9 | 2486.55 | 2593.67 | 2458.25 | 2644.74 | 2630.03
G10 | 2783.21 | 2777.83 | 2709.53 | 2823.31 | 2588.21
G11 | 2877.33 | 2944.37 | 2902.33 | 2849.05 | 1979.38
G12 | 2452.79 | 2514.21 | 2449.54 | 2568.88 | 2545.83
G13 | 2560.01 | 2602.35 | 2648.85 | 2692.01 | 2068.93
G14 | 2774.1 | 2745.59 | 2682.8 | 2323.67 | 1459.23
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 037 | Sammamish-Novelty Hill #2 230kV Line (PSE) (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6645.2193 | 385.91 | 473.8 | 570.9 | 1356.1 | 1470.47 | 1563.31 | 2785.25 | 2974.85 | 3021.95 | 2486.55 | 2783.21 | 2877.33 | 2452.79 | 2560.01 | 2774.1
35F | 6315.81 | 793.85 | 834.28 | 941.23 | 1644.85 | 1781.58 | 1921.28 | 2786.56 | 2947.14 | 3034.78 | 2593.67 | 2777.83 | 2944.37 | 2514.21 | 2602.35 | 2745.59
45F | 6031.17 | 488.41 | 553.66 | 664.18 | 1373.87 | 1475.99 | 1571.25 | 2723.57 | 2909.81 | 3100.76 | 2458.25 | 2709.53 | 2902.33 | 2449.54 | 2648.85 | 2682.8
60F | 4970.78 | 1815.17 | 1916.02 | 2028.9 | 2627.93 | 2730.05 | 2837.17 | 2821.32 | 3001.47 | 3177.43 | 2644.74 | 2823.31 | 2849.05 | 2568.88 | 2692.01 | 2323.67
70F | 4632.6447 | 2069.86 | 2141.14 | 2268.68 | 2858.45 | 2963.82 | 2899.84 | 2823.19 | 2996.66 | 2585.84 | 2630.03 | 2588.21 | 1979.38 | 2545.83 | 2068.93 | 1459.23

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 386.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 474.59 | 474.55 | 6656.58 | 385.91 | 104.11 | FULL
G1 | 473.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 474.06 | 473.98 | 6585.61 | 473.8 | 194.96 | FULL
G2 | 570.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 473.74 | 473.67 | 6597.21 | 570.9 | 284.13 | FULL
G3 | 1358.11 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 484.47 | 484.37 | 6653.31 | 1356.1 | 744.05 | FULL
G4 | 1472.9 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 485.02 | 485.02 | 6586 | 1470.47 | 840.86 | FULL
G5 | 1566.47 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 484.79 | 484.77 | 6599.38 | 1563.31 | 922.73 | FULL
G6 | 2797.3 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -14.33 | -514.62 | -514.52 | 6687.82 | 2785.25 | 1670.86 | FULL
G7 | 2988.73 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -517.38 | -517.32 | 6626.88 | 2974.85 | 1809.08 | FULL
G8 | 3037.16 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -508.01 | -507.79 | 6646.52 | 3021.95 | 1862.04 | FULL
G9 | 2495.99 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -14.33 | -508.34 | -508.07 | 6698.28 | 2486.55 | 1705.9 | FULL
G10 | 2795.33 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -514.67 | -514.63 | 6640.61 | 2783.21 | 1906.26 | FULL
G11 | 2890.61 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -514.16 | -513.84 | 6661.46 | 2877.33 | 1989.13 | FULL
G12 | 2461.47 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -14.34 | -516.33 | -516.42 | 6711.64 | 2452.79 | 1841.23 | FULL
G13 | 2569.98 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -506.96 | -506.87 | 6651.08 | 2560.01 | 1939.59 | FULL
G14 | 2786.22 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -507.07 | -507.02 | 6675.91 | 2774.1 | 2078.19 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 793.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 471.74 | 471.6 | 6321 | 793.85 | 385.49 | FULL
G1 | 835.65 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 469.96 | 469.76 | 6251.23 | 834.28 | 440.37 | FULL
G2 | 943.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 470.12 | 469.9 | 6263.87 | 941.23 | 534.98 | FULL
G3 | 1649.93 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 477.28 | 477.44 | 6324.01 | 1644.85 | 938.97 | FULL
G4 | 1784.94 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 478.57 | 478.59 | 6258.09 | 1781.58 | 1043.55 | FULL
G5 | 1926.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 480.07 | 480.19 | 6274.86 | 1921.28 | 1155.54 | FULL
G6 | 2798.93 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -504.07 | -503.99 | 6357.42 | 2786.56 | 1706.52 | FULL
G7 | 2960.55 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -501.11 | -500.98 | 6296.97 | 2947.14 | 1829.11 | FULL
G8 | 3050.18 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -499.09 | -498.96 | 6317.34 | 3034.78 | 1906.16 | FULL
G9 | 2604.06 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -14.33 | -500.66 | -500.75 | 6370.42 | 2593.67 | 1794.51 | FULL
G10 | 2789.95 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -503.24 | -503.17 | 6310.99 | 2777.83 | 1938.26 | FULL
G11 | 2958.64 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -504.18 | -504.06 | 6334.52 | 2944.37 | 2062.31 | FULL
G12 | 2524.12 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -501.75 | -501.59 | 6384.42 | 2514.21 | 1902.56 | FULL
G13 | 2612.93 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -498.9 | -498.64 | 6324.36 | 2602.35 | 1989.82 | FULL
G14 | 2757.58 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -499.84 | -500.64 | 6347.65 | 2745.59 | 2110.81 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 485.8 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 436.27 | 436.18 | 6037.08 | 488.41 | 214.88 | FULL
G1 | 552.87 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 435.43 | 435.29 | 5967.4 | 553.66 | 296.98 | FULL
G2 | 664.38 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 436.3 | 436.14 | 5979.67 | 664.18 | 393.48 | FULL
G3 | 1375.73 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 442.97 | 443.01 | 6037.73 | 1373.87 | 803.12 | FULL
G4 | 1478.5 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 442.91 | 441.97 | 5970.42 | 1475.99 | 894.59 | FULL
G5 | 1574.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 442.48 | 442.63 | 5985.25 | 1571.25 | 981.29 | FULL
G6 | 2734.09 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -483.53 | -483.39 | 6072.38 | 2723.57 | 1682.97 | FULL
G7 | 2923.09 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -485.86 | -485.72 | 6012.43 | 2909.81 | 1819.1 | FULL
G8 | 3115.39 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -489.07 | -488.97 | 6035.11 | 3100.76 | 1959.12 | FULL
G9 | 2467.76 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -482.15 | -481.92 | 6084.98 | 2458.25 | 1739.09 | FULL
G10 | 2720.39 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -483.15 | -483.17 | 6027.5 | 2709.53 | 1912.62 | FULL
G11 | 2916.5 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -486.76 | -486.64 | 6050.62 | 2902.33 | 2051.54 | FULL
G12 | 2458.34 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -483.61 | -483.49 | 6100.17 | 2449.54 | 1886.79 | FULL
G13 | 2659.99 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -488.35 | -488.24 | 6042.89 | 2648.85 | 2031.38 | FULL
G14 | 2693.96 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -477.51 | -477.31 | 6063.92 | 2682.8 | 2085.38 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1820 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 443.87 | 444.02 | 4965.49 | 1815.17 | 1095.5 | FULL
G1 | 1921.36 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 443.67 | 443.78 | 4901 | 1916.02 | 1194.26 | FULL
G2 | 2035.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 444.27 | 444.1 | 4919 | 2028.9 | 1289.02 | FULL
G3 | 2637.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 447.09 | 447.23 | 4987.55 | 2627.93 | 1623.75 | FULL
G4 | 2740.84 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 447.17 | 447.3 | 4925.32 | 2730.05 | 1713.45 | FULL
G5 | 2849.3 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 447.56 | 447.7 | 4946.19 | 2837.17 | 1799.05 | FULL
G6 | 2834.58 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -458.36 | -458.26 | 5005.46 | 2821.32 | 1847.51 | FULL
G7 | 3015.33 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -457.58 | -457.42 | 4947.74 | 3001.47 | 1980.08 | FULL
G8 | 3193.56 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -458.6 | -458.34 | 4974.67 | 3177.43 | 2106.4 | FULL
G9 | 2654.95 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -459.96 | -460.07 | 5023.23 | 2644.74 | 1946.14 | FULL
G10 | 2835.5 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -459.73 | -459.73 | 4966.82 | 2823.31 | 2084.78 | FULL
G11 | 2861.72 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -475.96 | -475.09 | 4986.56 | 2849.05 | 2129.37 | FULL
G12 | 2578.62 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -460.23 | -459.97 | 5041.96 | 2568.88 | 2054.78 | FULL
G13 | 2703.27 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -477.13 | -476.4 | 4984.79 | 2692.01 | 2161.9 | FULL
G14 | 2332.99 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -190.02 | -190.02 | 4985.92 | 2323.67 | 1981.92 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2076.22 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 445.43 | 445.57 | 4636.8 | 2069.86 | 1257.48 | FULL
G1 | 2147.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 444.37 | 444.46 | 4572.47 | 2141.14 | 1349.11 | FULL
G2 | 2277.82 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 445.17 | 445.22 | 4592.48 | 2268.68 | 1452.41 | FULL
G3 | 2870.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 448.33 | 447.44 | 4662.89 | 2858.45 | 1770.82 | FULL
G4 | 2975.56 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 447.87 | 447.82 | 4601.84 | 2963.82 | 1869.93 | FULL
G5 | 2912.54 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -173.03 | -173.02 | 4618.79 | 2899.84 | 1864.45 | FULL
G6 | 2835.27 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -443.22 | -443.14 | 4673.25 | 2823.19 | 1874.55 | FULL
G7 | 3010.7 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -442.83 | -442.58 | 4616.51 | 2996.66 | 2002.46 | FULL
G8 | 2595.67 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -173.65 | -173.58 | 4617.54 | 2585.84 | 1805.61 | FULL
G9 | 2640.4 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -441.8 | -441.87 | 4691.42 | 2630.03 | 1969.27 | FULL
G10 | 2598.35 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -172.25 | -172.25 | 4626.64 | 2588.21 | 1970.06 | FULL
G11 | 1985.94 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -173.15 | -173.14 | 4620.09 | 1979.38 | 1663.61 | FULL
G12 | 2556.32 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -442.45 | -442.39 | 4710.23 | 2545.83 | 2074.33 | FULL
G13 | 2076.25 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -172.71 | -172.73 | 4626.68 | 2068.93 | 1834.46 | FULL
G14 | 1463.43 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -173.58 | -173.57 | 4622.04 | 1459.23 | 1525.71 | FULL
037WINTER09v2NSH