## 25F nomo
Monroe-Novelty Hill (PSE) #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 029
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6645.128
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 388.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 605.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 505.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1559.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 605.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3021.79 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1357.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2882.06 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1473.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2778.82 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1559.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 505.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2785.27 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1473.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2972.06 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2972.06 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3021.79 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2690.71 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 2491.78 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2563.02 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2690.71 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 388.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2882.06 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1357.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2448.67 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2785.27 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2563.02 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2491.78 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 2778.82 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2448.67 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Monroe-Novelty Hill (PSE) #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 029
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6315.6267
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 789.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1008.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 841.46 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1911.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1008.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3049.4 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1644.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2952.38 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1780.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2749.1 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1911.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 841.46 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2787.37 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1780.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2975.91 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2975.91 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3049.4 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2684.02 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2592.44 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2607.9 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2684.02 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 789.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2952.38 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1644.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2419.35 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2787.37 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2607.9 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2592.44 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2749.1 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2419.35 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Monroe-Novelty Hill (PSE) #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 029
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6031.3887
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 486.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 705.4 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 602.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1570.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 705.4 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3102.65 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1372.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2905.4 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1475.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2738.06 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1570.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 602.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2723.12 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1475.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2912.31 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2912.31 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 3102.65 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2730.78 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2549.89 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2649.8 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2730.78 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 486.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2905.4 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1372.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2464.46 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2723.12 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2649.8 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2549.89 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2738.06 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2464.46 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Monroe-Novelty Hill (PSE) #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 029
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4970.334
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1821.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2022.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1935.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2828.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2022.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3078.39 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2627.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2848.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2728.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2323.22 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2828.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1935.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2822.68 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2728.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3003.83 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3003.83 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3078.39 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2827.65 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 2550.07 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2691.94 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2827.65 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1821.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2848.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2627.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2535.58 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2822.68 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 2691.94 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2550.07 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2323.22 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2535.58 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Monroe-Novelty Hill (PSE) #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 029
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4632.8173
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2066.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2258.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2168.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2900 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
100 | 775 | 2258.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2581.34 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2857.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2007.06 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2961.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1458.85 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2900 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2168.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2824.96 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2961.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2999.54 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2999.54 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2581.34 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2587.88 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2631.41 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2068.61 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2587.88 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2066.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2007.06 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2857.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2548.89 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2824.96 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2068.61 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2631.41 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1458.85 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2548.89 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Monroe-Novelty Hill (PSE) #1 230kV Line (COV-CRES BYP @ COV)
G0 | 388.54 | 789.82 | 486.19 | 1821.76 | 2066.12
G1 | 505.83 | 841.46 | 602.56 | 1935.24 | 2168.6 | Season/Year: | WINTER 2009
G2 | 605.81 | 1008.28 | 705.4 | 2022.29 | 2258.89 | Direction: | North-to-South (NS)
G3 | 1357.16 | 1644.2 | 1372.76 | 2627.19 | 2857.6 | Case Loads: | Heavy Loads
G4 | 1473.94 | 1780.29 | 1475.71 | 2728.78 | 2961.3 | Outage: | 029
G5 | 1559.64 | 1911.05 | 1570.83 | 2828.17 | 2900 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2785.27 | 2787.37 | 2723.12 | 2822.68 | 2824.96 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2972.06 | 2975.91 | 2912.31 | 3003.83 | 2999.54 | Study Person: | FRP9899
G8 | 3021.79 | 3049.4 | 3102.65 | 3078.39 | 2581.34 | Source: | 029WINTER09v2NSH
G9 | 2491.78 | 2592.44 | 2549.89 | 2550.07 | 2631.41
G10 | 2690.71 | 2684.02 | 2730.78 | 2827.65 | 2587.88
G11 | 2882.06 | 2952.38 | 2905.4 | 2848.75 | 2007.06
G12 | 2448.67 | 2419.35 | 2464.46 | 2535.58 | 2548.89
G13 | 2563.02 | 2607.9 | 2649.8 | 2691.94 | 2068.61
G14 | 2778.82 | 2749.1 | 2738.06 | 2323.22 | 1458.85
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 029 | Monroe-Novelty Hill (PSE) #1 230kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6645.128 | 388.54 | 505.83 | 605.81 | 1357.16 | 1473.94 | 1559.64 | 2785.27 | 2972.06 | 3021.79 | 2491.78 | 2690.71 | 2882.06 | 2448.67 | 2563.02 | 2778.82
35F | 6315.6267 | 789.82 | 841.46 | 1008.28 | 1644.2 | 1780.29 | 1911.05 | 2787.37 | 2975.91 | 3049.4 | 2592.44 | 2684.02 | 2952.38 | 2419.35 | 2607.9 | 2749.1
45F | 6031.3887 | 486.19 | 602.56 | 705.4 | 1372.76 | 1475.71 | 1570.83 | 2723.12 | 2912.31 | 3102.65 | 2549.89 | 2730.78 | 2905.4 | 2464.46 | 2649.8 | 2738.06
60F | 4970.334 | 1821.76 | 1935.24 | 2022.29 | 2627.19 | 2728.78 | 2828.17 | 2822.68 | 3003.83 | 3078.39 | 2550.07 | 2827.65 | 2848.75 | 2535.58 | 2691.94 | 2323.22
70F | 4632.8173 | 2066.12 | 2168.6 | 2258.89 | 2857.6 | 2961.3 | 2900 | 2824.96 | 2999.54 | 2581.34 | 2631.41 | 2587.88 | 2007.06 | 2548.89 | 2068.61 | 1458.85

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 388.85 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 474.78 | 474.53 | 6656.54 | 388.54 | 105.91 | FULL
G1 | 505.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 475.29 | 475.21 | 6585.37 | 505.83 | 207.64 | FULL
G2 | 605.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 474.72 | 474.66 | 6596.87 | 605.81 | 298.16 | FULL
G3 | 1358.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 484.57 | 484.38 | 6653.32 | 1357.16 | 744.82 | FULL
G4 | 1476.39 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 485.31 | 485.06 | 6585.94 | 1473.94 | 843.18 | FULL
G5 | 1562.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 484.5 | 484.76 | 6599.29 | 1559.64 | 920.78 | FULL
G6 | 2796.8 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -14.33 | -514.02 | -513.93 | 6688.11 | 2785.27 | 1670.26 | FULL
G7 | 2986.03 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -516.6 | -516.67 | 6626.84 | 2972.06 | 1807.68 | FULL
G8 | 3037.04 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -512.95 | -514.2 | 6647.27 | 3021.79 | 1866.93 | FULL
G9 | 2501.22 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -14.33 | -508.61 | -508.36 | 6698.44 | 2491.78 | 1708.65 | FULL
G10 | 2702.76 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -511.27 | -510.94 | 6638.49 | 2690.71 | 1851.53 | FULL
G11 | 2895.42 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -514.14 | -513.8 | 6661.61 | 2882.06 | 1991.41 | FULL
G12 | 2458.25 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -14.34 | -515.92 | -515.74 | 6711.52 | 2448.67 | 1838.37 | FULL
G13 | 2573.04 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -506.99 | -506.89 | 6651.19 | 2563.02 | 1941.53 | FULL
G14 | 2790.57 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -507.37 | -507.26 | 6676.12 | 2778.82 | 2080.95 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 789.39 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 471.6 | 471.46 | 6321.14 | 789.82 | 383.11 | FULL
G1 | 842.33 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 469.76 | 469.55 | 6252.24 | 841.46 | 438.12 | FULL
G2 | 1007.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 472.15 | 472 | 6264.79 | 1008.28 | 574.02 | FULL
G3 | 1649.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 477.29 | 477.45 | 6324 | 1644.2 | 938.75 | FULL
G4 | 1783.7 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 478.45 | 478.59 | 6258.07 | 1780.29 | 1042.95 | FULL
G5 | 1915.48 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 479.78 | 479.78 | 6274.34 | 1911.05 | 1152.97 | FULL
G6 | 2799.4 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -505.32 | -505.24 | 6357.26 | 2787.37 | 1707.58 | FULL
G7 | 2990.47 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -504.21 | -504.01 | 6296.95 | 2975.91 | 1836.19 | FULL
G8 | 3064.5 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -500.71 | -500.53 | 6317.12 | 3049.4 | 1927.61 | FULL
G9 | 2602.83 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -500.66 | -500.63 | 6370.44 | 2592.44 | 1793.93 | FULL
G10 | 2695.37 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -498.78 | -498.47 | 6308.99 | 2684.02 | 1883.92 | FULL
G11 | 2966.05 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -503.53 | -503.3 | 6334.9 | 2952.38 | 2066.78 | FULL
G12 | 2428.77 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -498.35 | -498.62 | 6382.25 | 2419.35 | 1856.52 | FULL
G13 | 2618.06 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -499.24 | -498.95 | 6324.14 | 2607.9 | 1992.88 | FULL
G14 | 2760.88 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -500.08 | -499.89 | 6347.77 | 2749.1 | 2112.92 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 483.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 436.23 | 436.14 | 6037.19 | 486.19 | 213.5 | FULL
G1 | 602.22 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 437.25 | 437.12 | 5967.15 | 602.56 | 315.08 | FULL
G2 | 706.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 437.37 | 437.25 | 5979.53 | 705.4 | 407.6 | FULL
G3 | 1376.38 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 442.92 | 443.02 | 6037.73 | 1372.76 | 802.6 | FULL
G4 | 1478.11 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 442.93 | 441.98 | 5970.43 | 1475.71 | 894.56 | FULL
G5 | 1574.42 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 442.48 | 442.64 | 5985.25 | 1570.83 | 981.18 | FULL
G6 | 2734.75 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -483.55 | -483.54 | 6072.28 | 2723.12 | 1683.09 | FULL
G7 | 2926.24 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -485.99 | -485.71 | 6012.47 | 2912.31 | 1820.71 | FULL
G8 | 3117.42 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -489.02 | -488.91 | 6035.16 | 3102.65 | 1960.33 | FULL
G9 | 2559.2 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -484.91 | -484.67 | 6086.46 | 2549.89 | 1783.15 | FULL
G10 | 2742.64 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -487.67 | -487.78 | 6027.17 | 2730.78 | 1925.24 | FULL
G11 | 2918.18 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -486.45 | -486.36 | 6050.71 | 2905.4 | 2054.51 | FULL
G12 | 2475.8 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -486.81 | -486.76 | 6100.44 | 2464.46 | 1888.58 | FULL
G13 | 2661.16 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -488.24 | -488.16 | 6042.93 | 2649.8 | 2032.06 | FULL
G14 | 2749.58 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -480.93 | -480.62 | 6065.93 | 2738.06 | 2108.56 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1827.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 443.93 | 444.05 | 4965.63 | 1821.76 | 1099.32 | FULL
G1 | 1940.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 444.23 | 444.39 | 4901.29 | 1935.24 | 1197.46 | FULL
G2 | 2029.24 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 444.61 | 444.45 | 4918.67 | 2022.29 | 1278.99 | FULL
G3 | 2636.49 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 447.1 | 447.24 | 4987.59 | 2627.19 | 1623.56 | FULL
G4 | 2740.2 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 447.2 | 447.31 | 4925.28 | 2728.78 | 1712.86 | FULL
G5 | 2840.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 447.56 | 447.65 | 4945.67 | 2828.17 | 1798.89 | FULL
G6 | 2835.93 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -458.3 | -458.2 | 5005.47 | 2822.68 | 1848.37 | FULL
G7 | 3017.72 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -457.64 | -457.49 | 4947.81 | 3003.83 | 1981.54 | FULL
G8 | 3093.32 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -456.63 | -456.43 | 4970.32 | 3078.39 | 2054.11 | FULL
G9 | 2559.99 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -454.09 | -454.03 | 5021.69 | 2550.07 | 1899.02 | FULL
G10 | 2839.85 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -459.97 | -460.03 | 4967 | 2827.65 | 2086.69 | FULL
G11 | 2861.6 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -475.93 | -475.07 | 4986.57 | 2848.75 | 2129.32 | FULL
G12 | 2545.1 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -456.65 | -456.54 | 5041.31 | 2535.58 | 2043.93 | FULL
G13 | 2703.21 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -477.12 | -476.39 | 4984.79 | 2691.94 | 2162.01 | FULL
G14 | 2332.54 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -189.97 | -189.97 | 4985.92 | 2323.22 | 1981.78 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2073.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 445.04 | 445.15 | 4636.84 | 2066.12 | 1255.4 | FULL
G1 | 2176.29 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 445.38 | 445.17 | 4574.14 | 2168.6 | 1346.81 | FULL
G2 | 2267.67 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 445.04 | 445.16 | 4592.93 | 2258.89 | 1429.5 | FULL
G3 | 2870 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 448.32 | 447.42 | 4662.86 | 2857.6 | 1770.5 | FULL
G4 | 2975.86 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.59 | 447.87 | 447.91 | 4601.75 | 2961.3 | 1868.56 | FULL
G5 | 2912.96 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -172.96 | -172.96 | 4618.71 | 2900 | 1865.2 | FULL
G6 | 2837.24 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -443.26 | -443.17 | 4673.3 | 2824.96 | 1875.67 | FULL
G7 | 3013.59 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -442.91 | -442.68 | 4616.59 | 2999.54 | 2004.15 | FULL
G8 | 2591.63 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -173.4 | -173.4 | 4617.31 | 2581.34 | 1803.76 | FULL
G9 | 2641.91 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -14.39 | -441.74 | -441.81 | 4691.37 | 2631.41 | 1970.22 | FULL
G10 | 2598.02 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -172.21 | -172.2 | 4626.65 | 2587.88 | 1970 | FULL
G11 | 2012.01 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -173.88 | -173.83 | 4620.74 | 2007.06 | 1685.95 | FULL
G12 | 2558.35 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.39 | -442.52 | -442.42 | 4710.35 | 2548.89 | 2076.17 | FULL
G13 | 2075.93 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -172.66 | -172.68 | 4626.68 | 2068.61 | 1834.4 | FULL
G14 | 1463.06 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -173.53 | -173.52 | 4622.04 | 1458.85 | 1525.6 | FULL
029WINTER09v2NSH