## 25F nomo
Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 002
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6692.7514
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1397.37 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2109.9 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2202.48 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2496.58 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2109.9 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3018.51 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1789.53 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3604.04 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2535.47 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3628.16 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV]
260 | 775 | 2496.58 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2202.48 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2689.53 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2535.47 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3003.39 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3003.39 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3018.51 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3578.34 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3339.9 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3617.66 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1000 | 460 | 3578.34 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1397.37 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3604.04 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1789.53 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 2422.67 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2689.53 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3617.66 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G10 | 1000 | 140 | 3339.9 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 3628.16 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] |  |  | G13 | 1400 | 140 | 2422.67 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 002
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6363.4392
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2391.44 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2223.31 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2252.65 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2571.38 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2223.31 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3077.15 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2457.91 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3538.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2606.08 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3560.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2571.38 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2252.65 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2832.78 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2606.08 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3094 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3094 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3077.15 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3519.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3345.05 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3564.64 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1000 | 460 | 3519.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2391.44 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3538.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2457.91 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 3565.69 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G7 | 525 | 140 | 2832.78 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3564.64 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G10 | 1000 | 140 | 3345.05 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 3560.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 3565.69 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 002
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 5989.8308
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2352.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2022.62 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2057.21 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2310.8 | N-1: Monroe - Custer #1 500kV | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2022.62 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2956.49 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2618.12 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3428.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2578.14 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2925.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2310.8 | N-1: Monroe - Custer #1 500kV | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2057.21 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2943.02 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2578.14 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2979.41 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2979.41 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2956.49 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3422.23 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3400.92 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 3019.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3422.23 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2352.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3428.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2618.12 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 3109.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2943.02 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3019.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3400.92 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 2925.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 3109.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 002
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4915.3269
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2276.49 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2112.22 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2130.91 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2393.3 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2112.22 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2838.48 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2551.17 | N-1: Monroe - Custer #1 500kV | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3163.18 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2547.34 | N-1: Monroe - Custer #1 500kV | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1640.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2393.3 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 2130.91 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2804.63 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2547.34 | N-1: Monroe - Custer #1 500kV | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2812.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2812.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2838.48 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3137.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3124.18 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1749.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3137.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2276.49 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3163.18 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2551.17 | N-1: Monroe - Custer #1 500kV | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1856.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2804.63 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1749.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3124.18 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1640.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1856.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 002
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4631.2867
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2122.24 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2066.39 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2095.11 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2296.45 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2066.39 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2673.9 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2331.81 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3064.53 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2328.24 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1386.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2296.45 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2095.11 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2637.04 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2328.24 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2686.2 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2686.2 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2673.9 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3040.46 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3007.01 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1481.57 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3040.46 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2122.24 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3064.53 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2331.81 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1591.26 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2637.04 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1481.57 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3007.01 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1386.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1591.26 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
G0 | 1397.37 | 2391.44 | 2352.64 | 2276.49 | 2122.24
G1 | 2202.48 | 2252.65 | 2057.21 | 2130.91 | 2095.11 | Season/Year: | WINTER 2009
G2 | 2109.9 | 2223.31 | 2022.62 | 2112.22 | 2066.39 | Direction: | South-to-North (SN)
G3 | 1789.53 | 2457.91 | 2618.12 | 2551.17 | 2331.81 | Case Loads: | Heavy Loads
G4 | 2535.47 | 2606.08 | 2578.14 | 2547.34 | 2328.24 | Outage: | 002
G5 | 2496.58 | 2571.38 | 2310.8 | 2393.3 | 2296.45 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2689.53 | 2832.78 | 2943.02 | 2804.63 | 2637.04 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3003.39 | 3094 | 2979.41 | 2812.71 | 2686.2 | Study Person: | JGO7470
G8 | 3018.51 | 3077.15 | 2956.49 | 2838.48 | 2673.9 | Source: | 002WINTER09v2SNH(SN@100MW)
G9 | 3339.9 | 3345.05 | 3400.92 | 3124.18 | 3007.01
G10 | 3578.34 | 3519.42 | 3422.23 | 3137.2 | 3040.46
G11 | 3604.04 | 3538.42 | 3428.33 | 3163.18 | 3064.53
G12 | 2422.67 | 3565.69 | 3109.35 | 1856.84 | 1591.26
G13 | 3617.66 | 3564.64 | 3019.96 | 1749.3 | 1481.57
G14 | 3628.16 | 3560.63 | 2925.45 | 1640.81 | 1386.23
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 002 | Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6692.7514 | 1398.1 | 2202.25 | 2109.67 | 1787.72 | 2535.3 | 2496.13 | 2688.9 | 3002.93 | 3018.16 | 3339.25 | 3578 | 3603.52 | 2423.42 | 3619.29 | 3627.65
35F | 6363.4392 | 2390.23 | 2252.41 | 2222.99 | 2457.47 | 2606.03 | 2571.07 | 2832.42 | 3091.69 | 3076.87 | 3344.48 | 3518.82 | 3537.82 | 3563.62 | 3565 | 3559.36
45F | 5989.8308 | 2352.26 | 2056.74 | 2022.99 | 2617.2 | 2577.31 | 2310.06 | 2942.94 | 2979.08 | 2956.09 | 3398.32 | 3421.6 | 3427.72 | 3108.81 | 3019.6 | 2925.35
60F | 4915.3269 | 2274.36 | 2131.34 | 2112.39 | 2550.89 | 2546.55 | 2393 | 2804.32 | 2812.49 | 2838.93 | 3123.78 | 3138.45 | 3161.01 | 1855.28 | 1746.59 | 1640.78
70F | 4631.2867 | 2122.31 | 2095.11 | 2065.78 | 2330.01 | 2328.66 | 2296.73 | 2636.59 | 2685.74 | 2671.85 | 3005.58 | 3039.92 | 3063.96 | 1591.25 | 1479.54 | 1386.36

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1397.37 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | -3.45 | -533.94 | -533.98 | 6700.56 | 1398.1 | -1022.21 | FULL
G1 | 2202.48 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | -9.2 | -504.35 | -504.54 | 6659.62 | 2202.25 | -1461.81 | FULL
G2 | 2109.9 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | -9.2 | -493.23 | -493.13 | 6664.48 | 2109.67 | -1374.21 | FULL
G3 | 1789.53 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -3.4 | -537.08 | -537.14 | 6708.92 | 1787.72 | -1176.07 | FULL
G4 | 2535.47 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | -9.2 | -490.89 | -490.74 | 6668.07 | 2535.3 | -1590.2 | FULL
G5 | 2496.58 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | -9.2 | -504.31 | -504.23 | 6674.25 | 2496.13 | -1539.41 | FULL
G6 | 2689.53 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 12.22 | 622.65 | 634.28 | 6736.19 | 2688.9 | -1581.24 | CTG_FAIL_IN_FULL
G7 | 3003.39 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | -9.2 | -484.7 | -484.8 | 6679.52 | 3002.93 | -1748.67 | FULL
G8 | 3018.51 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.1 | -675.1 | -675.08 | 6686.07 | 3018.16 | -1722.51 | CTG_FAIL_IN_FULL
G9 | 3339.9 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.29 | 536.24 | 536.25 | 6746.67 | 3339.25 | -1742.54 | CTG_FAIL_IN_FULL
G10 | 3578.34 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.57 | -2688.86 | -2688.73 | 6688.4 | 3578 | -1863.16 | CTG_FAIL_IN_FULL
G11 | 3604.04 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.57 | -2696.33 | -2696.26 | 6696.62 | 3603.52 | -1847.51 | CTG_FAIL_IN_FULL
G12 | 2422.67 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.98 | 397.81 | 503.04 | 6721.01 | 2423.42 | -1046.13 | CTG_FAIL_IN_FULL
G13 | 3617.66 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3577.93 | 3576.4 | 6680.08 | 3619.29 | -1731.19 | FULL
G14 | 3628.16 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | -100 | -3589.44 | -3588.03 | 6688.62 | 3627.65 | -1708.54 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2391.44 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -3.4 | -533.34 | -533.26 | 6403.48 | 2390.23 | -1565.54 | FULL
G1 | 2252.65 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | -9.2 | -474.63 | -474.78 | 6324.95 | 2252.41 | -1457.71 | FULL
G2 | 2223.31 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | -9.2 | -478.73 | -478.8 | 6331.22 | 2222.99 | -1410.31 | FULL
G3 | 2457.91 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -3.4 | -515.78 | -536.5 | 6401.46 | 2457.47 | -1521.53 | FULL
G4 | 2606.08 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | -9.2 | -492.03 | -491.95 | 6334 | 2606.03 | -1593.23 | FULL
G5 | 2571.38 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | -9.2 | -492.2 | -492.44 | 6341.11 | 2571.07 | -1544.31 | FULL
G6 | 2832.78 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 12.22 | 610.32 | 597.53 | 6404.67 | 2832.42 | -1623.47 | CTG_FAIL_IN_FULL
G7 | 3094 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.1 | -667.94 | -668.4 | 6346.2 | 3091.69 | -1743.51 | CTG_FAIL_IN_FULL
G8 | 3077.15 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.1 | -669.68 | -669.66 | 6351.99 | 3076.87 | -1716.57 | CTG_FAIL_IN_FULL
G9 | 3345.05 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 12.69 | 600.16 | 583.07 | 6412.55 | 3344.48 | -1709.46 | CTG_FAIL_IN_FULL
G10 | 3519.42 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.57 | -2617.88 | -2619.46 | 6346.67 | 3518.82 | -1789.18 | CTG_FAIL_IN_FULL
G11 | 3538.42 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.57 | -2622.32 | -2622.45 | 6356.41 | 3537.82 | -1774.16 | CTG_FAIL_IN_FULL
G12 | 3565.69 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3529.25 | 3530.85 | 6411.7 | 3563.62 | -1681.23 | FULL
G13 | 3564.64 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3528.82 | 3530.5 | 6339.6 | 3565 | -1653.99 | FULL
G14 | 3560.63 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -471.18 | -471.14 | 6347.13 | 3559.36 | -1623.35 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2352.64 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -15.27 | -636.89 | -636.96 | 6112.94 | 2352.26 | -1523.57 | CTG_FAIL_IN_FULL
G1 | 2057.21 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -16.08 | -593.99 | -594.23 | 6030.49 | 2056.74 | -1324.14 | FULL
G2 | 2022.62 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -16.08 | -595.63 | -595.4 | 6038.26 | 2022.99 | -1266.24 | FULL
G3 | 2618.12 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.1 | -637 | -636.87 | 6118.23 | 2617.2 | -1610.32 | CTG_FAIL_IN_FULL
G4 | 2578.14 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.1 | -637.38 | -637.26 | 6043.06 | 2577.31 | -1561.84 | CTG_FAIL_IN_FULL
G5 | 2310.8 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | N-1: Monroe - Custer #1 500kV | -16.82 | -601.35 | -601.02 | 6044.12 | 2310.06 | -1366.35 | FULL
G6 | 2943.02 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.29 | 504.91 | 504.88 | 6122.21 | 2942.94 | -1676.43 | CTG_FAIL_IN_FULL
G7 | 2979.41 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.1 | -638.93 | -638.91 | 6051.13 | 2979.08 | -1673.78 | CTG_FAIL_IN_FULL
G8 | 2956.49 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.1 | -640.3 | -640.29 | 6058.81 | 2956.09 | -1634.42 | CTG_FAIL_IN_FULL
G9 | 3400.92 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.57 | -2533.03 | -2534.82 | 6127.61 | 3398.32 | -1732.18 | CTG_FAIL_IN_FULL
G10 | 3422.23 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.57 | -2543.21 | -2543.24 | 6054.48 | 3421.6 | -1716.39 | CTG_FAIL_IN_FULL
G11 | 3428.33 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.57 | -2531.97 | -2532.05 | 6063.97 | 3427.72 | -1693.53 | CTG_FAIL_IN_FULL
G12 | 3109.35 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -437.2 | -437.17 | 6103.38 | 3108.81 | -1404.76 | FULL
G13 | 3019.96 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -435.48 | -435.44 | 6027.35 | 3019.6 | -1315.17 | FULL
G14 | 2925.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -433.69 | -433.64 | 6034.8 | 2925.35 | -1233.15 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2276.49 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -16.08 | -572.77 | -572.82 | 5018.65 | 2274.36 | -1359.4 | FULL
G1 | 2130.91 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.91 | -557.5 | -557.85 | 4942.8 | 2131.34 | -1241.99 | FULL
G2 | 2112.22 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.91 | -560.15 | -560.32 | 4952.68 | 2112.39 | -1200.7 | FULL
G3 | 2551.17 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | N-1: Monroe - Custer #1 500kV | -16.82 | -577.04 | -577.35 | 5024.43 | 2550.89 | -1451.15 | FULL
G4 | 2547.34 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | N-1: Monroe - Custer #1 500kV | -16.82 | -586.92 | -586.97 | 4951.22 | 2546.55 | -1414.1 | FULL
G5 | 2393.3 | Branch HORSRNCH (42320) TO HRTAP MS (40963) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.91 | -568.61 | -568.19 | 4957.83 | 2393 | -1294.37 | FULL
G6 | 2804.63 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.04 | -2229.27 | -2230.91 | 5025.02 | 2804.32 | -1470.71 | FULL
G7 | 2812.71 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.04 | -2221.26 | -2222.65 | 4956.31 | 2812.49 | -1455.37 | FULL
G8 | 2838.48 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.04 | -2231.63 | -2233.23 | 4968.6 | 2838.93 | -1439.96 | FULL
G9 | 3124.18 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.04 | -2228.88 | -2230.02 | 5027.98 | 3123.78 | -1452.17 | FULL
G10 | 3137.2 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.04 | -2225.95 | -2226.96 | 4957.77 | 3138.45 | -1422.43 | FULL
G11 | 3163.18 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.04 | -2237.83 | -2238.64 | 4969.29 | 3161.01 | -1410.43 | FULL
G12 | 1856.84 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -420.46 | -420.42 | 4979.91 | 1855.28 | -526.48 | FULL
G13 | 1749.3 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -419.23 | -419.15 | 4909.37 | 1746.59 | -431.24 | FULL
G14 | 1640.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -417.94 | -417.82 | 4921.32 | 1640.78 | -337.89 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2122.24 | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 16.91 | 538.34 | 538.1 | 4673.29 | 2122.31 | -1233.51 | FULL
G1 | 2095.11 | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 16.91 | 541.94 | 542.33 | 4601.34 | 2095.11 | -1186.6 | FULL
G2 | 2066.39 | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 16.91 | 541.96 | 542.45 | 4611.94 | 2065.78 | -1140 | FULL
G3 | 2331.81 | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 16.91 | 538.29 | 538.5 | 4678.43 | 2330.01 | -1281.99 | FULL
G4 | 2328.24 | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 16.91 | 540.39 | 540.06 | 4607.09 | 2328.66 | -1260.45 | FULL
G5 | 2296.45 | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 16.91 | 541.61 | 541.29 | 4617.54 | 2296.73 | -1209.13 | FULL
G6 | 2637.04 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -67.63 | -2102.96 | -2103.95 | 4683.03 | 2636.59 | -1342.39 | FULL
G7 | 2686.2 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -67.63 | -2128.7 | -2130.32 | 4613.7 | 2685.74 | -1337.16 | FULL
G8 | 2673.9 | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 16.91 | 540.77 | 540.94 | 4624.77 | 2671.85 | -1305.65 | FULL
G9 | 3007.01 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -67.63 | -2134.19 | -2133.45 | 4685.65 | 3005.58 | -1335.49 | FULL
G10 | 3040.46 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -67.63 | -2152.19 | -2154.04 | 4615.38 | 3039.92 | -1332.34 | FULL
G11 | 3064.53 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -67.63 | -2146.63 | -2145.85 | 4628.26 | 3063.96 | -1317.71 | FULL
G12 | 1591.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -416.78 | -416.66 | 4641.15 | 1591.25 | -340.75 | FULL
G13 | 1481.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -415.74 | -415.62 | 4572.1 | 1479.54 | -243.51 | FULL
G14 | 1386.23 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -415.89 | -415.79 | 4585.77 | 1386.36 | -156.94 | FULL
002WINTER09v2SNH(SN@100MW)