## 25F nomo
Snohomish-Murray #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 043
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3340.4913
Gen Level |  | Trans | Worst | Limiting |  |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [6 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3416.81 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G3 | 100 | 775 | 3423.88 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3434.33 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G6 | 260 | 775 | 3267.28 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3423.88 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G9 | 525 | 775 | 2989.01 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3267.26 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G12 | 1000 | 775 | 2577.29 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3276.2 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G15 | 1400 | 775 | 2430.03 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3267.28 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G2 | 100 | 465 | 3434.33 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2982.93 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G5 | 260 | 460 | 3276.2 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2987.84 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G8 | 525 | 460 | 2987.84 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2989.01 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G11 | 1000 | 460 | 2575.53 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2578.21 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G14 | 1400 | 460 | 2423.64 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2575.53 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G1 | 100 | 140 | 3416.81 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2577.29 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G4 | 260 | 140 | 3267.26 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2414.95 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G7 | 525 | 140 | 2982.93 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2423.64 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G10 | 1000 | 140 | 2578.21 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2430.03 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  |  | G13 | 1400 | 140 | 2414.95 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450
G1
789

## 35F nomo
Snohomish-Murray #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 043
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2661.8813
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3257.75 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3259.82 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3259.7 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3101.71 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3259.82 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2825.78 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3102.43 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2396.79 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3101.51 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2260.8 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3101.71 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3259.7 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2821.63 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3101.51 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2823.86 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2823.86 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2825.78 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2405.19 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2404.51 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2249.87 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2405.19 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3257.75 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2396.79 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 3102.43 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2257.55 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2821.63 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2249.87 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2404.51 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2260.8 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2257.55 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Snohomish-Murray #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 043
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2420.446
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3137.24 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3134.1 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3138.05 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2967.76 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3134.1 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2693.21 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2968.1 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2265.86 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2966.01 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2115.96 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2967.76 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3138.05 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2697.09 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2966.01 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2688.41 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2688.41 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2693.21 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2263.55 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2264.36 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2116.43 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2263.55 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3137.24 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2265.86 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2968.1 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2113.3 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2697.09 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2116.43 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2264.36 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2115.96 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2113.3 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Snohomish-Murray #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 043
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2940.352
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3102.36 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3115.85 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3111.2 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2936.99 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3115.85 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2666.94 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2945.25 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2239.44 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2944.73 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2084.91 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2936.99 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 3111.2 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2659.06 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2944.73 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2665.6 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2665.6 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2666.94 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2235.66 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2231.46 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2086.69 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2235.66 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3102.36 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2239.44 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2945.25 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2097.09 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2659.06 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2086.69 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2231.46 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2084.91 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2097.09 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Snohomish-Murray #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 043
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3291.8347
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3049.95 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3058.12 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3052.19 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2890.55 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3058.12 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2608.26 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2883.26 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2181.42 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2886.44 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2029.66 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2890.55 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3052.19 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2600.67 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2886.44 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2613.38 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2613.38 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2608.26 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2177.53 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2174.14 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2025.98 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2177.53 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3049.95 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2181.42 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2883.26 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2000.75 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2600.67 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2025.98 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2174.14 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2029.66 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2000.75 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Snohomish-Murray #1 230kV Line (COV-CRES BYP @ COV)
G0 | 3416.81 | 3257.75 | 3137.24 | 3102.36 | 3049.95
G1 | 3434.33 | 3259.7 | 3138.05 | 3111.2 | 3052.19 | Season/Year: | WINTER 2009
G2 | 3423.88 | 3259.82 | 3134.1 | 3115.85 | 3058.12 | Direction: | North-to-South (NS)
G3 | 3267.26 | 3102.43 | 2968.1 | 2945.25 | 2883.26 | Case Loads: | Light Loads
G4 | 3276.2 | 3101.51 | 2966.01 | 2944.73 | 2886.44 | Outage: | 043
G5 | 3267.28 | 3101.71 | 2967.76 | 2936.99 | 2890.55 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2982.93 | 2821.63 | 2697.09 | 2659.06 | 2600.67 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2987.84 | 2823.86 | 2688.41 | 2665.6 | 2613.38 | Study Person: | FRP9899
G8 | 2989.01 | 2825.78 | 2693.21 | 2666.94 | 2608.26 | Source: | 043WINTER09v2NSL(SN@100MW)
G9 | 2578.21 | 2404.51 | 2264.36 | 2231.46 | 2174.14
G10 | 2575.53 | 2405.19 | 2263.55 | 2235.66 | 2177.53
G11 | 2577.29 | 2396.79 | 2265.86 | 2239.44 | 2181.42
G12 | 2414.95 | 2257.55 | 2113.3 | 2097.09 | 2000.75
G13 | 2423.64 | 2249.87 | 2116.43 | 2086.69 | 2025.98
G14 | 2430.03 | 2260.8 | 2115.96 | 2084.91 | 2029.66
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Light Loads |  |  | 043 | Snohomish-Murray #1 230kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3340.4913 | 3416.81 | 3434.33 | 3423.88 | 3267.26 | 3276.2 | 3267.28 | 2982.93 | 2987.84 | 2989.01 | 2578.21 | 2575.53 | 2577.29 | 2414.95 | 2423.64 | 2430.03
35F | 2661.8813 | 3257.75 | 3259.7 | 3259.82 | 3102.43 | 3101.51 | 3101.71 | 2821.63 | 2823.86 | 2825.78 | 2404.51 | 2405.19 | 2396.79 | 2257.55 | 2249.87 | 2260.8
45F | 2420.446 | 3137.24 | 3138.05 | 3134.1 | 2968.1 | 2966.01 | 2967.76 | 2697.09 | 2688.41 | 2693.21 | 2264.36 | 2263.55 | 2265.86 | 2113.3 | 2116.43 | 2115.96
60F | 2940.352 | 3102.36 | 3111.2 | 3115.85 | 2945.25 | 2944.73 | 2936.99 | 2659.06 | 2665.6 | 2666.94 | 2231.46 | 2235.66 | 2239.44 | 2097.09 | 2086.69 | 2084.91
70F | 3291.8347 | 3049.95 | 3052.19 | 3058.12 | 2883.26 | 2886.44 | 2890.55 | 2600.67 | 2613.38 | 2608.26 | 2174.14 | 2177.53 | 2181.42 | 2000.75 | 2025.98 | 2029.66

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3435.72 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.86 | -786.39 | -788.35 | 3370.29 | 3416.81 | 1710.98 | FULL
G1 | 3453.53 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.86 | -799.84 | -801.63 | 3306.97 | 3434.33 | 1741 | FULL
G2 | 3442.6 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.86 | -787.92 | -788.08 | 3325.1 | 3423.88 | 1765.46 | FULL
G3 | 3284.45 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.86 | -812.48 | -813.47 | 3368.02 | 3267.26 | 1685.27 | FULL
G4 | 3293.54 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.86 | -815.96 | -816.92 | 3305.28 | 3276.2 | 1722.87 | FULL
G5 | 3284.37 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.86 | -811.14 | -811.92 | 3323.43 | 3267.28 | 1742.38 | FULL
G6 | 2996.98 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.86 | -818.78 | -819.38 | 3369.71 | 2982.93 | 1637.97 | FULL
G7 | 3002.08 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.86 | -816.78 | -817.54 | 3306.19 | 2987.84 | 1669.21 | FULL
G8 | 3002.77 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.86 | -817.43 | -818.21 | 3324.51 | 2989.01 | 1701.11 | FULL
G9 | 2587.98 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -843.86 | -842.97 | 3378.71 | 2578.21 | 1629.13 | FULL
G10 | 2585.76 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -840.12 | -839.48 | 3314.86 | 2575.53 | 1648.06 | FULL
G11 | 2587.15 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -838.99 | -838.34 | 3333.58 | 2577.29 | 1683.84 | FULL
G12 | 2423.6 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -833.37 | -832.91 | 3396.02 | 2414.95 | 1683.51 | FULL
G13 | 2432.09 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -833.78 | -834.7 | 3332.9 | 2423.64 | 1721.11 | FULL
G14 | 2438.62 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -841.48 | -841.09 | 3351.8 | 2430.03 | 1747.87 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3274.77 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.86 | -791.3 | -790.8 | 2690.11 | 3257.75 | 1673.38 | FULL
G1 | 3277.13 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.86 | -791.29 | -790.93 | 2626.29 | 3259.7 | 1703.91 | FULL
G2 | 3276.32 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.86 | -790.31 | -790 | 2646.03 | 3259.82 | 1724.74 | FULL
G3 | 3117.79 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -811.69 | -810.39 | 2687.51 | 3102.43 | 1653.81 | FULL
G4 | 3116.55 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -807.61 | -806.43 | 2625.41 | 3101.51 | 1679.29 | FULL
G5 | 3116.82 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -807.78 | -806.5 | 2644.35 | 3101.71 | 1707.52 | FULL
G6 | 2834.02 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -812.57 | -811.38 | 2689.34 | 2821.63 | 1613.73 | FULL
G7 | 2836.47 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -812.25 | -811.39 | 2626.82 | 2823.86 | 1641.71 | FULL
G8 | 2838 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -814.68 | -813.71 | 2646.45 | 2825.78 | 1666.3 | FULL
G9 | 2412.62 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -823.76 | -822.46 | 2700.22 | 2404.51 | 1585.38 | FULL
G10 | 2414.31 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -820.69 | -819.45 | 2637.06 | 2405.19 | 1614.85 | FULL
G11 | 2404.8 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -816.46 | -815.26 | 2657.52 | 2396.79 | 1628.76 | FULL
G12 | 2265.45 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -825.64 | -824.35 | 2718.39 | 2257.55 | 1657.49 | FULL
G13 | 2257.71 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -814.73 | -813.52 | 2656.38 | 2249.87 | 1672.28 | FULL
G14 | 2268.29 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -825.29 | -824.02 | 2676.34 | 2260.8 | 1703.14 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3152.37 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -780.04 | -780.55 | 2447.41 | 3137.24 | 1633.46 | FULL
G1 | 3153.4 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -775.46 | -773.68 | 2384.16 | 3138.05 | 1669.15 | FULL
G2 | 3149.6 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -773.71 | -772.9 | 2403.7 | 3134.1 | 1693.29 | FULL
G3 | 2981.62 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -787.96 | -787.49 | 2446.45 | 2968.1 | 1602.55 | FULL
G4 | 2979.89 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -785.92 | -785.4 | 2383.15 | 2966.01 | 1635.02 | FULL
G5 | 2980.81 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -783.13 | -781.98 | 2402.93 | 2967.76 | 1663.24 | FULL
G6 | 2708.01 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -792.67 | -791.03 | 2448.19 | 2697.09 | 1575.5 | FULL
G7 | 2699.33 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -783.2 | -782.15 | 2385.02 | 2688.41 | 1600.21 | FULL
G8 | 2704.17 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -787.67 | -786 | 2404.68 | 2693.21 | 1629.38 | FULL
G9 | 2271.19 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -789.59 | -788.2 | 2459.12 | 2264.36 | 1541.21 | FULL
G10 | 2270.92 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -786.71 | -785.28 | 2396.76 | 2263.55 | 1563.52 | FULL
G11 | 2272.42 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -787.72 | -786.27 | 2415.96 | 2265.86 | 1598.64 | FULL
G12 | 2118.69 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -782.85 | -781.08 | 2477.85 | 2113.3 | 1610.56 | FULL
G13 | 2122.19 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -783.79 | -782.77 | 2415.41 | 2116.43 | 1630.63 | FULL
G14 | 2121.66 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -785.22 | -783.8 | 2435.9 | 2115.96 | 1658.98 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3117.37 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -718.43 | -717.82 | 2968.77 | 3102.36 | 1582.39 | FULL
G1 | 3126.1 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -721.7 | -720.93 | 2905.14 | 3111.2 | 1615.62 | FULL
G2 | 3130.91 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -727.67 | -726.53 | 2924.13 | 3115.85 | 1639.86 | FULL
G3 | 2958.92 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -737.93 | -735.94 | 2967.6 | 2945.25 | 1557.43 | FULL
G4 | 2957.78 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -734.86 | -733 | 2903.43 | 2944.73 | 1588.14 | FULL
G5 | 2950.95 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -728.51 | -726.57 | 2921.97 | 2936.99 | 1603.35 | FULL
G6 | 2669.73 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -732.55 | -731 | 2969.31 | 2659.06 | 1518.6 | FULL
G7 | 2676.5 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -731.87 | -730.4 | 2905.81 | 2665.6 | 1549.93 | FULL
G8 | 2677.46 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -734.09 | -732.47 | 2924.29 | 2666.94 | 1569.1 | FULL
G9 | 2238.78 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -731.75 | -730.2 | 2979.79 | 2231.46 | 1487.05 | FULL
G10 | 2243.18 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -731.9 | -730.37 | 2916.6 | 2235.66 | 1517.23 | FULL
G11 | 2246.22 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -738.01 | -736.44 | 2934.64 | 2239.44 | 1542.83 | FULL
G12 | 2102.78 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -740.75 | -738.75 | 2996.84 | 2097.09 | 1563.69 | FULL
G13 | 2092.74 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -731.84 | -731.41 | 2934.23 | 2086.69 | 1583.1 | FULL
G14 | 2091.43 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -730.83 | -730.85 | 2952.73 | 2084.91 | 1615.35 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3064.7 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -688.71 | -688.07 | 3320.04 | 3049.95 | 1549.23 | FULL
G1 | 3067.7 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -687.83 | -687.15 | 3256.94 | 3052.19 | 1560.17 | FULL
G2 | 3072.49 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -691.76 | -691.09 | 3275.31 | 3058.12 | 1603.73 | FULL
G3 | 2895.81 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -695.08 | -693.23 | 3319.23 | 2883.26 | 1514.09 | FULL
G4 | 2899 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -694.43 | -692.54 | 3255.38 | 2886.44 | 1544.23 | FULL
G5 | 2903.5 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -703.48 | -703.11 | 3273.55 | 2890.55 | 1578.43 | FULL
G6 | 2610.77 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -696.82 | -695.24 | 3321.43 | 2600.67 | 1465.68 | FULL
G7 | 2623.2 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -702.9 | -701.2 | 3257.85 | 2613.38 | 1510.34 | FULL
G8 | 2618.78 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -699.72 | -698.04 | 3275.14 | 2608.26 | 1544.14 | FULL
G9 | 2180.38 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -695.73 | -694.36 | 3331.7 | 2174.14 | 1445.72 | FULL
G10 | 2184.18 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -697.97 | -696.68 | 3268.57 | 2177.53 | 1464.03 | FULL
G11 | 2188.4 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -699.64 | -698.3 | 3286.64 | 2181.42 | 1494.86 | FULL
G12 | 2006.39 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -697.89 | -696.25 | 3347.6 | 2000.75 | 1502.51 | FULL
G13 | 2031.04 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -697.14 | -695.39 | 3285 | 2025.98 | 1543.66 | FULL
G14 | 2034.96 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -67.5 | -697.4 | -695.64 | 3303.14 | 2029.66 | 1576.26 | FULL
043WINTER09v2NSL(SN@100MW)