## 25F nomo
Schultz-Echo Lake #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 038
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6636.5773
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 502.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 716.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 526.53 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1628.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 716.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3363.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1403.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2695.02 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1498.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2329.98 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1628.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 526.53 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2926.81 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1498.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3292.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3292.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3363.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3014.92 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1000 | 140 | 2765.05 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3042.4 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3014.92 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 502.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2695.02 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1403.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2883.06 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2926.81 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1400 | 460 | 3042.4 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2765.05 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1400 | 775 | 2329.98 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2883.06 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Schultz-Echo Lake #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 038
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6313.002
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 827.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1061.67 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 916.26 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1949.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1061.67 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3515.03 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1724.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3108.87 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1840.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2421.55 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1949.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 916.26 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3385.52 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1840.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3499.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3499.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3515.03 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3097.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3094.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2966.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3097.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 827.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3108.87 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1724.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2948.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3385.52 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2966.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3094.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2421.55 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2948.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Schultz-Echo Lake #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 038
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6027.63
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 589.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 797.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 645.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1650.18 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 797.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3338.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1428.4 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3057.84 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1537 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2722.91 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1650.18 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 645.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3164.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1537 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3254.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3254.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3338.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3047.74 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3036.87 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2906.19 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3047.74 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 589.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3057.84 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1428.4 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2891.14 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3164.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2906.19 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3036.87 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2722.91 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2891.14 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Schultz-Echo Lake #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 038
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4967.3747
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1890.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2075.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1973.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2858.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2075.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3260.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2654.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2845.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2757.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2449.93 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2858.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1973.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3238.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2757.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3248.82 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3248.82 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3260.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2827.24 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2817.7 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2687.18 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2827.24 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1890.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2845.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2654.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2649.55 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3238.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2687.18 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2817.7 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2449.93 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2649.55 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Schultz-Echo Lake #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 038
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4630.2847
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2105.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2305.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2199.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2986.55 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
100 | 775 | 2305.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2657.6 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2901.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2081.68 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2998.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1560.8 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2986.55 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2199.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3162.65 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2998.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3170.9 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3170.9 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2657.6 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2710.79 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2751.66 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2168.95 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2710.79 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2105.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2081.68 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2901.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2525.35 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3162.65 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2168.95 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2751.66 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1560.8 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2525.35 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Schultz-Echo Lake #1 500kV Line (COV-CRES BYP @ COV)
G0 | 502.94 | 827.7 | 589.35 | 1890.34 | 2105.05
G1 | 526.53 | 916.26 | 645.72 | 1973.36 | 2199.89 | Season/Year: | WINTER 2009
G2 | 716.43 | 1061.67 | 797.28 | 2075.36 | 2305.68 | Direction: | North-to-South (NS)
G3 | 1403.88 | 1724.7 | 1428.4 | 2654.95 | 2901.75 | Case Loads: | Heavy Loads
G4 | 1498.17 | 1840.06 | 1537 | 2757.14 | 2998.82 | Outage: | 038
G5 | 1628.63 | 1949.92 | 1650.18 | 2858.58 | 2986.55 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2926.81 | 3385.52 | 3164.58 | 3238.86 | 3162.65 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3292.02 | 3499.49 | 3254.81 | 3248.82 | 3170.9 | Study Person: | FRP9899
G8 | 3363.64 | 3515.03 | 3338.7 | 3260.21 | 2657.6 | Source: | 038WINTER09v2NSH
G9 | 2765.05 | 3094.29 | 3036.87 | 2817.7 | 2751.66
G10 | 3014.92 | 3097.01 | 3047.74 | 2827.24 | 2710.79
G11 | 2695.02 | 3108.87 | 3057.84 | 2845.97 | 2081.68
G12 | 2883.06 | 2948.73 | 2891.14 | 2649.55 | 2525.35
G13 | 3042.4 | 2966.2 | 2906.19 | 2687.18 | 2168.95
G14 | 2329.98 | 2421.55 | 2722.91 | 2449.93 | 1560.8
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 038 | Schultz-Echo Lake #1 500kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6636.5773 | 502.94 | 526.53 | 716.43 | 1403.88 | 1498.17 | 1628.63 | 2926.81 | 3292.02 | 3363.64 | 2765.05 | 3014.92 | 2695.02 | 2883.06 | 3042.4 | 2329.98
35F | 6313.002 | 827.7 | 916.26 | 1061.67 | 1724.7 | 1840.06 | 1949.92 | 3385.52 | 3499.49 | 3515.03 | 3094.29 | 3097.01 | 3108.87 | 2948.73 | 2966.2 | 2421.55
45F | 6027.63 | 589.35 | 645.72 | 797.28 | 1428.4 | 1537 | 1650.18 | 3164.58 | 3254.81 | 3338.7 | 3036.87 | 3047.74 | 3057.84 | 2891.14 | 2906.19 | 2722.91
60F | 4967.3747 | 1890.34 | 1973.36 | 2075.36 | 2654.95 | 2757.14 | 2858.58 | 3238.86 | 3248.82 | 3260.21 | 2817.7 | 2827.24 | 2845.97 | 2649.55 | 2687.18 | 2449.93
70F | 4630.2847 | 2105.05 | 2199.89 | 2305.68 | 2901.75 | 2998.82 | 2986.55 | 3162.65 | 3170.9 | 2657.6 | 2751.66 | 2710.79 | 2081.68 | 2525.35 | 2168.95 | 1560.8

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 502.43 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 476.92 | 476.86 | 6635.41 | 502.94 | 304.95 | FULL
G1 | 525.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 473.99 | 473.92 | 6566.98 | 526.53 | 348.54 | FULL
G2 | 716.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 477.56 | 477.5 | 6580.38 | 716.43 | 473.06 | FULL
G3 | 1405.98 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 484.87 | 484.75 | 6636.76 | 1403.88 | 854.19 | FULL
G4 | 1501.22 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 484.64 | 484.62 | 6570.62 | 1498.17 | 940.34 | FULL
G5 | 1630.95 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 486.09 | 486.03 | 6586.6 | 1628.63 | 1027.58 | FULL
G6 | 2941.9 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | 30.17 | 1337.03 | 1337.86 | 6684.57 | 2926.81 | 1791.07 | FULL
G7 | 3308.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 492.3 | 492.32 | 6627 | 3292.02 | 2011.85 | FULL
G8 | 3382.39 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 490.46 | 490.72 | 6646.11 | 3363.64 | 2071.96 | FULL
G9 | 2779.33 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | 30.17 | 1346.48 | 1333.29 | 6703.75 | 2765.05 | 1891.06 | FULL
G10 | 3030.22 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | 30.17 | 1369.87 | 1392.94 | 6644.31 | 3014.92 | 2049.32 | FULL
G11 | 2705.75 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 3 | 457.11 | 457.06 | 6640.49 | 2695.02 | 1912.85 | FULL
G12 | 2896.22 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | 30.17 | 1418.99 | 1410.19 | 6722.48 | 2883.06 | 2091.48 | FULL
G13 | 3057.21 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -512.41 | -511.8 | 6660.1 | 3042.4 | 2189.65 | FULL
G14 | 2337.76 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 3.01 | 458.74 | 458.78 | 6643.1 | 2329.98 | 1858.78 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 827.35 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 471.05 | 470.91 | 6303.51 | 827.7 | 523.7 | FULL
G1 | 918.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 471.21 | 471.01 | 6235.56 | 916.26 | 588.7 | FULL
G2 | 1061.46 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 472.88 | 472.73 | 6250.83 | 1061.67 | 696.01 | FULL
G3 | 1729.07 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 478.56 | 478.69 | 6310.61 | 1724.7 | 1059.64 | FULL
G4 | 1844.12 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 479.16 | 479.23 | 6245.74 | 1840.06 | 1146.61 | FULL
G5 | 1955.02 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 479.78 | 479.86 | 6262.65 | 1949.92 | 1230.44 | FULL
G6 | 3403.53 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -10.4 | -504.43 | -506.39 | 6370.54 | 3385.52 | 2064.46 | CTG_FAIL_IN_FULL
G7 | 3519.88 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -490.97 | -490.03 | 6308.4 | 3499.49 | 2146.17 | FULL
G8 | 3536.13 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -490.1 | -489.85 | 6328.18 | 3515.03 | 2176.68 | FULL
G9 | 3109.39 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -500.9 | -500.19 | 6381.51 | 3094.29 | 2099.87 | FULL
G10 | 3112.73 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -500.72 | -499.96 | 6317.32 | 3097.01 | 2122.26 | FULL
G11 | 3124.79 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -500.2 | -499.48 | 6332.09 | 3108.87 | 2153.85 | FULL
G12 | 2962.42 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -501.12 | -500.97 | 6395.32 | 2948.73 | 2161.48 | FULL
G13 | 2980.07 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -503.4 | -503.13 | 6330.96 | 2966.2 | 2196.4 | FULL
G14 | 2430.63 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 3.01 | 457.84 | 457.76 | 6321.81 | 2421.55 | 1926.98 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 588.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 438.17 | 438.09 | 6019.82 | 589.35 | 399.62 | FULL
G1 | 645.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 437.03 | 436.9 | 5951.49 | 645.72 | 449.01 | FULL
G2 | 797.12 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 438.57 | 438.5 | 5965.47 | 797.28 | 562.61 | FULL
G3 | 1432.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 442.69 | 442.8 | 6023.47 | 1428.4 | 907.69 | FULL
G4 | 1541.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 443.1 | 443.35 | 5958.01 | 1537 | 991.25 | FULL
G5 | 1652.99 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 443.6 | 443.86 | 5974.4 | 1650.18 | 1077.41 | FULL
G6 | 3181.03 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 446.33 | 446.56 | 6077.85 | 3164.58 | 1949.47 | FULL
G7 | 3272.4 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 446.76 | 446.86 | 6015.41 | 3254.81 | 2032.32 | FULL
G8 | 3356.43 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 446.26 | 446.21 | 6036.66 | 3338.7 | 2092.72 | FULL
G9 | 3051.33 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -491.73 | -491.34 | 6097.3 | 3036.87 | 2076.44 | FULL
G10 | 3062.52 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -492.13 | -491.68 | 6032.66 | 3047.74 | 2106.53 | FULL
G11 | 3072.77 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -491.35 | -491 | 6050.13 | 3057.84 | 2134.72 | FULL
G12 | 2904.1 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -492.26 | -491.61 | 6110.98 | 2891.14 | 2140.03 | FULL
G13 | 2919.99 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -495.17 | -494.57 | 6046.63 | 2906.19 | 2171.18 | FULL
G14 | 2734.32 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 3 | 459.76 | 459.81 | 6054.17 | 2722.91 | 2091.88 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1897.11 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 445 | 445.12 | 4956.73 | 1890.34 | 1193.03 | FULL
G1 | 1980.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 444.6 | 444.68 | 4893.06 | 1973.36 | 1257.6 | FULL
G2 | 2082.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 444.87 | 444.98 | 4911.89 | 2075.36 | 1338.88 | FULL
G3 | 2665.46 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 447.33 | 447.4 | 4979.83 | 2654.95 | 1651.41 | FULL
G4 | 2768.18 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 447.62 | 447.72 | 4918.93 | 2757.14 | 1729.69 | FULL
G5 | 2871.03 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 447.75 | 447.81 | 4939.89 | 2858.58 | 1809.17 | FULL
G6 | 3255.82 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.69 | -474.77 | -475.75 | 5016.41 | 3238.86 | 2064.49 | FULL
G7 | 3265.9 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -472.05 | -472.1 | 4953.53 | 3248.82 | 2093.64 | FULL
G8 | 3276.92 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -469.96 | -470.52 | 4971.55 | 3260.21 | 2124.39 | FULL
G9 | 2829.93 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.69 | -476.55 | -475.8 | 5024.66 | 2817.7 | 2026.64 | FULL
G10 | 2839.76 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.69 | -476.31 | -475.55 | 4961.42 | 2827.24 | 2056.02 | FULL
G11 | 2858.4 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.69 | -476.22 | -475.46 | 4979.74 | 2845.97 | 2098.11 | FULL
G12 | 2660.39 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -12.88 | -457.6 | -457.49 | 5040.15 | 2649.55 | 2074.16 | FULL
G13 | 2697.98 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.69 | -477.16 | -476.5 | 4977.35 | 2687.18 | 2129.14 | FULL
G14 | 2459.2 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.62 | -191.36 | -191.33 | 4985.48 | 2449.93 | 2022.2 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2111.75 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 444.76 | 444.87 | 4629.19 | 2105.05 | 1321.17 | FULL
G1 | 2206.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 445.13 | 445.24 | 4566.33 | 2199.89 | 1391.36 | FULL
G2 | 2315.44 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 444.97 | 445.12 | 4586.84 | 2305.68 | 1478.21 | FULL
G3 | 2914.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 447.78 | 447.81 | 4657.4 | 2901.75 | 1799.04 | FULL
G4 | 3012.88 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.61 | 448.01 | 448.02 | 4597.51 | 2998.82 | 1874.27 | FULL
G5 | 3000.16 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.62 | -174.5 | -174.49 | 4615.41 | 2986.55 | 1891.9 | FULL
G6 | 3178.83 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.69 | -460.56 | -459.55 | 4682.75 | 3162.65 | 2039.38 | FULL
G7 | 3187.07 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.69 | -459.5 | -459.18 | 4619.85 | 3170.9 | 2067.88 | FULL
G8 | 2668.56 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.62 | -173.53 | -173.45 | 4615.04 | 2657.6 | 1827.35 | FULL
G9 | 2763.16 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.69 | -462.75 | -461.86 | 4690.31 | 2751.66 | 2023.75 | FULL
G10 | 2722.1 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.62 | -173.94 | -173.87 | 4625.73 | 2710.79 | 2026.76 | FULL
G11 | 2088.45 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.62 | -175.72 | -175.74 | 4618.05 | 2081.68 | 1714.73 | FULL
G12 | 2535.02 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -12.88 | -443.49 | -443.46 | 4705.23 | 2525.35 | 2034.29 | FULL
G13 | 2175.13 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.62 | -173.47 | -173.42 | 4625.27 | 2168.95 | 1875.06 | FULL
G14 | 1564.88 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.62 | -173.31 | -173.3 | 4619.36 | 1560.8 | 1583.85 | FULL
038WINTER09v2NSH