## 25F nomo
Covington 230kV West Bus O/S
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 198
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6557.6067
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 407.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 621.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 522.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1637.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 621.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3370.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1406.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3057.17 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
260 | 460 | 1528.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 3100.14 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1637.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 522.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2973.46 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1528.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3243.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3243.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3370.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3221.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2941.18 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3078.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3221.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 407.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3057.17 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1406.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 3072.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2973.46 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1400 | 460 | 3078.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2941.18 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1400 | 775 | 3100.14 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 3072.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Covington 230kV West Bus O/S
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 198
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6424.8313
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 627.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 794.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 683.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1755.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 794.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3442.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1524.26 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3163.08 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1639.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 3026.55 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1755.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 683.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3259.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1639.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3356.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3356.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3442.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3158.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3050.2 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3016.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3158.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 627.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3163.08 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1524.26 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 3012.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3259.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 3016.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3050.2 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1400 | 775 | 3026.55 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 3012.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Covington 230kV West Bus O/S
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 198
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 5981.264
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 502.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 726.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 615.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1629.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 726.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3091.37 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1431.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2615.6 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 1524.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2210.23 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1629.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 615.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3118.84 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1524.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3253.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3253.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3091.37 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2962.29 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 3067.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2533.91 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 2962.29 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 502.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2615.6 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1431.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2930.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3118.84 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1400 | 460 | 2533.91 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3067.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2210.23 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2930.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Covington 230kV West Bus O/S
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 198
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4917.742
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1828.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1750.2 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1934.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1584.19 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1750.2 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1329 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2272.99 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 839.79 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 1920.96 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 444.99 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1584.19 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 1934.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2001.54 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1920.96 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 1668.72 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1668.72 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1329 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1177.63 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1527.77 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 770.6 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 1177.63 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1828.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 839.79 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2272.99 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1121.94 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2001.54 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 770.6 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1527.77 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 444.99 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1121.94 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Covington 230kV West Bus O/S
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 198
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4582.9427
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1549.95 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 869.87 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1202.04 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 702.44 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 869.87 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 438.62 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1383.96 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | -39.6 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 1033.98 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -443.74 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 702.44 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1202.04 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 1120.9 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1033.98 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 771.98 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 771.98 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 438.62 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 295.03 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 643.55 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | -111.29 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 295.03 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1549.95 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | -39.6 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1383.96 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 236.71 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1120.9 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | -111.29 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 643.55 | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | -443.74 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 236.71 | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Covington 230kV West Bus O/S
G0 | 407.39 | 627.88 | 502.71 | 1828.05 | 1549.95
G1 | 522.77 | 683.72 | 615.17 | 1934.96 | 1202.04 | Season/Year: | WINTER 2009
G2 | 621.89 | 794.78 | 726.63 | 1750.2 | 869.87 | Direction: | North-to-South (NS)
G3 | 1406.41 | 1524.26 | 1431.34 | 2272.99 | 1383.96 | Case Loads: | Heavy Loads
G4 | 1528.51 | 1639.03 | 1524.03 | 1920.96 | 1033.98 | Outage: | 198
G5 | 1637.63 | 1755.27 | 1629.21 | 1584.19 | 702.44 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2973.46 | 3259.54 | 3118.84 | 2001.54 | 1120.9 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3243.95 | 3356.92 | 3253.01 | 1668.72 | 771.98 | Study Person: | FRP9899
G8 | 3370.3 | 3442.96 | 3091.37 | 1329 | 438.62 | Source: | 198WINTER09v5NSH
G9 | 2941.18 | 3050.2 | 3067.26 | 1527.77 | 643.55
G10 | 3221.26 | 3158.42 | 2962.29 | 1177.63 | 295.03
G11 | 3057.17 | 3163.08 | 2615.6 | 839.79 | -39.6
G12 | 3072.25 | 3012.97 | 2930.28 | 1121.94 | 236.71
G13 | 3078.92 | 3016.25 | 2533.91 | 770.6 | -111.29
G14 | 3100.14 | 3026.55 | 2210.23 | 444.99 | -443.74
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 198 | Covington 230kV West Bus O/S
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6557.6067 | 407.39 | 522.77 | 621.89 | 1406.41 | 1528.51 | 1637.63 | 2973.46 | 3243.95 | 3370.3 | 2941.18 | 3221.26 | 3057.17 | 3072.25 | 3078.92 | 3100.14
35F | 6424.8313 | 627.88 | 683.72 | 794.78 | 1524.26 | 1639.03 | 1755.27 | 3259.54 | 3356.92 | 3442.96 | 3050.2 | 3158.42 | 3163.08 | 3012.97 | 3016.25 | 3026.55
45F | 5981.264 | 502.71 | 615.17 | 726.63 | 1431.34 | 1524.03 | 1629.21 | 3118.84 | 3253.01 | 3091.37 | 3067.26 | 2962.29 | 2615.6 | 2930.28 | 2533.91 | 2210.23
60F | 4917.742 | 1828.05 | 1934.96 | 1750.2 | 2272.99 | 1920.96 | 1584.19 | 2001.54 | 1668.72 | 1329 | 1527.77 | 1177.63 | 839.79 | 1121.94 | 770.6 | 444.99
70F | 4582.9427 | 1549.95 | 1202.04 | 869.87 | 1383.96 | 1033.98 | 702.44 | 1120.9 | 771.98 | 438.62 | 643.55 | 295.03 | -39.6 | 236.71 | -111.29 | -443.74

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 406.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 475.03 | 474.96 | 6561.2 | 407.39 | -1.84 | FULL
G1 | 524.33 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 474.83 | 474.78 | 6490.05 | 522.77 | 95.27 | FULL
G2 | 621.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 475.23 | 475.15 | 6501.72 | 621.89 | 182.61 | FULL
G3 | 1409.22 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 485.87 | 485.85 | 6557.83 | 1406.41 | 627.44 | FULL
G4 | 1529.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 486.35 | 486.16 | 6489.93 | 1528.51 | 731.65 | FULL
G5 | 1641.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 486.7 | 486.61 | 6504.04 | 1637.63 | 822.45 | FULL
G6 | 2988.45 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 31.35 | 1262.79 | 1265.31 | 6599.23 | 2973.46 | 1593.24 | FULL
G7 | 3260.54 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 489.39 | 489.43 | 6538.21 | 3243.95 | 1771.5 | FULL
G8 | 3388.69 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 490.31 | 490.07 | 6558.6 | 3370.3 | 1895.4 | FULL
G9 | 2955.79 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 31.35 | 1310.25 | 1393.5 | 6622.3 | 2941.18 | 1781.94 | CTG_FAIL_IN_FULL
G10 | 3238.28 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -508.56 | -508.02 | 6562.29 | 3221.26 | 1967.68 | FULL
G11 | 3073.01 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 31.35 | 1294.24 | 1207.41 | 6574.04 | 3057.17 | 1911.49 | FULL
G12 | 3086.44 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -511.74 | -511.12 | 6639.81 | 3072.25 | 2003.1 | FULL
G13 | 3094 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -513.56 | -512.97 | 6573.75 | 3078.92 | 2035.04 | FULL
G14 | 3115.69 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -513.08 | -512.51 | 6591.1 | 3100.14 | 2083.12 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 627.46 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 470.28 | 470.07 | 6424.27 | 627.88 | 159.31 | FULL
G1 | 684.88 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 468.96 | 468.91 | 6354.22 | 683.72 | 213.2 | FULL
G2 | 794.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 469.17 | 469.13 | 6366.44 | 794.78 | 306.79 | FULL
G3 | 1525.39 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 477.25 | 477.05 | 6423.78 | 1524.26 | 719 | FULL
G4 | 1642.84 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 477.62 | 477.76 | 6356.73 | 1639.03 | 813.87 | FULL
G5 | 1759.4 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 478.1 | 478.24 | 6371.74 | 1755.27 | 909.72 | FULL
G6 | 3276.97 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 481.44 | 481.61 | 6471.96 | 3259.54 | 1801.57 | FULL
G7 | 3374.88 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 480.07 | 480.32 | 6410.51 | 3356.92 | 1871.4 | FULL
G8 | 3462.16 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 479.77 | 479.52 | 6430.03 | 3442.96 | 1947.16 | FULL
G9 | 3065.5 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 31.35 | 1333.2 | 1385.56 | 6490.48 | 3050.2 | 1868.68 | FULL
G10 | 3175.7 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -501.48 | -500.83 | 6426.87 | 3158.42 | 1965.81 | FULL
G11 | 3179.75 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -499.15 | -498.52 | 6443.39 | 3163.08 | 1990.33 | FULL
G12 | 3026.99 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -502.18 | -501.9 | 6504.5 | 3012.97 | 2008.9 | FULL
G13 | 3030.58 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -501.39 | -501.11 | 6440.52 | 3016.25 | 2023.64 | FULL
G14 | 3040.92 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -500.31 | -500.04 | 6457.03 | 3026.55 | 2064.14 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 500.99 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 436.43 | 436.33 | 5983.51 | 502.71 | 106.59 | FULL
G1 | 614.37 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 436.69 | 436.59 | 5913.74 | 615.17 | 201.91 | FULL
G2 | 727.94 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 437.56 | 437.45 | 5926.18 | 726.63 | 295.56 | FULL
G3 | 1432.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 443.56 | 443.71 | 5984.13 | 1431.34 | 693.22 | FULL
G4 | 1526.02 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 442.92 | 442.77 | 5916.73 | 1524.03 | 776.35 | FULL
G5 | 1633.56 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 443.22 | 443.38 | 5932.02 | 1629.21 | 865.29 | FULL
G6 | 3134.1 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 31.35 | 1251.83 | 1268.54 | 6030.43 | 3118.84 | 1734.6 | FULL
G7 | 3269.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 445.61 | 445.54 | 5969.27 | 3253.01 | 1844.3 | FULL
G8 | 3106.27 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 661.08 | 661.06 | 5983.8 | 3091.37 | 1782.63 | FULL
G9 | 3082.36 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -491.71 | -491.31 | 6052.73 | 3067.26 | 1906.19 | FULL
G10 | 2976.71 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 661.44 | 661.39 | 5984.62 | 2962.29 | 1865.81 | FULL
G11 | 2628.37 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | 4.21 | 661.39 | 661.44 | 5992.69 | 2615.6 | 1705.57 | FULL
G12 | 2943.53 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -493.65 | -492.98 | 6065.59 | 2930.28 | 1989.21 | FULL
G13 | 2545.33 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | 4.21 | 661.89 | 661.83 | 5990.37 | 2533.91 | 1779.2 | FULL
G14 | 2219.16 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 662.46 | 662.42 | 5993.15 | 2210.23 | 1644.59 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1834.53 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 444.33 | 444.5 | 4945.35 | 1828.05 | 959.82 | FULL
G1 | 1940.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.55 | 444.54 | 444.65 | 4880.76 | 1934.96 | 1062.01 | FULL
G2 | 1754.62 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 630.92 | 630.9 | 4895.84 | 1750.2 | 987.03 | FULL
G3 | 2281.85 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | 4.21 | 630.19 | 630.16 | 4961.25 | 2272.99 | 1265.68 | FULL
G4 | 1929.2 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 630.57 | 630.54 | 4889.24 | 1920.96 | 1102.25 | FULL
G5 | 1589.31 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 631.1 | 631.08 | 4897.07 | 1584.19 | 955.06 | FULL
G6 | 2009.02 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | 4.21 | 630.55 | 630.51 | 4964.55 | 2001.54 | 1230.63 | FULL
G7 | 1674.02 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | 4.21 | 631.17 | 631.14 | 4889.19 | 1668.72 | 1085.16 | FULL
G8 | 1332.57 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | 4.21 | 631.25 | 631.22 | 4897.39 | 1329 | 922.18 | FULL
G9 | 1532.13 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 630.89 | 630.86 | 4968.82 | 1527.77 | 1176.79 | FULL
G10 | 1180.09 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 631.04 | 631.01 | 4894.11 | 1177.63 | 1008.87 | FULL
G11 | 840 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 631.22 | 631.2 | 4902.45 | 839.79 | 853.47 | FULL
G12 | 1124.02 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 630.89 | 630.87 | 4973.36 | 1121.94 | 1097.55 | FULL
G13 | 771.4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 631.2 | 631.18 | 4898.88 | 770.6 | 935.05 | FULL
G14 | 444.69 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | 4.21 | 631.56 | 631.54 | 4907.87 | 444.99 | 786.91 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1554.12 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 608.76 | 608.71 | 4623.86 | 1549.95 | 847.11 | FULL
G1 | 1204.46 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 609 | 608.98 | 4552.25 | 1202.04 | 683.55 | FULL
G2 | 872.04 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 609.19 | 609.18 | 4563.72 | 869.87 | 527.69 | FULL
G3 | 1388.28 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 608.9 | 608.87 | 4622.65 | 1383.96 | 816.7 | FULL
G4 | 1035.55 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 609.13 | 609.11 | 4550.76 | 1033.98 | 653.05 | FULL
G5 | 704.03 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | 4.21 | 609.35 | 609.33 | 4562.56 | 702.44 | 497.49 | FULL
G6 | 1122.6 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 608.95 | 608.93 | 4622.88 | 1120.9 | 779.55 | FULL
G7 | 773.7 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | 4.21 | 609.41 | 609.4 | 4551.13 | 771.98 | 623.77 | FULL
G8 | 438.22 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | 4.21 | 609.56 | 609.54 | 4562.81 | 438.62 | 467.54 | FULL
G9 | 643.62 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | 4.21 | 609.33 | 609.3 | 4628.43 | 643.55 | 723.14 | FULL
G10 | 293.16 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 609.57 | 609.56 | 4557.2 | 295.03 | 559.76 | FULL
G11 | -41.07 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4311 Tacoma-Raver 500kV & Raver Reactor 2 | 4.21 | 609.7 | 609.69 | 4569.2 | -39.6 | 403.16 | FULL
G12 | 236 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 609.46 | 609.44 | 4634.25 | 236.71 | 647.33 | FULL
G13 | -112.42 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 609.67 | 609.66 | 4564.25 | -111.29 | 485.33 | FULL
G14 | -444.86 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: 4308 Tacoma-Raver 500kV & Raver Reactor 3&4 | 4.21 | 609.7 | 609.69 | 4578.19 | -443.74 | 334.5 | FULL
198WINTER09v5NSH