## 25F nomo
Chief Joseph-Snohomish #3 or #4 operating at 230kV (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 013
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6464.6593
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 287.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 507.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 405.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1529.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 507.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3323.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1299.57 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2922.64 | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1418.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2443.62 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1529.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 405.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3090.72 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1418.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3193.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3193.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3323.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3196.13 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3040.18 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3050.44 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3196.13 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 287.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2922.64 | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1299.57 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 3037.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3090.72 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1400 | 460 | 3050.44 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3040.18 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1400 | 775 | 2443.62 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 3037.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Chief Joseph-Snohomish #3 or #4 operating at 230kV (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 013
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6150.4293
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 648.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 883.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 766.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1829.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 883.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3516.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1588.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3108.76 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1712.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2813.18 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1829.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 766.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3342.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1712.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3361.73 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3361.73 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
525 | 775 | 3516.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3093.16 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3093.62 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2959.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3093.16 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 648.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3108.76 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1588.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2949.24 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3342.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2959.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3093.62 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2813.18 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2949.24 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Chief Joseph-Snohomish #3 or #4 operating at 230kV (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 013
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 5867.504
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 395.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 628.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 510.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1535.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 628.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3259.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1331.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3051.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1451.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2844.43 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1535.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 510.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3086.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1451.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3179.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3179.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3259.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3040.33 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3030.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2898.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3040.33 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 395.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3051.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1331.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2886.57 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3086.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2898.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3030.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2844.43 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2886.57 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Chief Joseph-Snohomish #3 or #4 operating at 230kV (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 013
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4840.6613
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1762.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1996.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1896.66 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2816.07 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1996.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3254.78 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2593.18 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2851.94 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2711.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2480.05 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2816.07 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1896.66 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3237.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2711.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3240.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3240.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3254.78 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2828.72 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2820.05 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2686.58 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2828.72 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1762.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2851.94 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2593.18 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2652.77 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3237.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2686.58 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2820.05 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2480.05 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2652.77 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Chief Joseph-Snohomish #3 or #4 operating at 230kV (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 013
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4511.2333
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2024.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2238.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2151.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 3036.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2238.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2748.27 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2833.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2168.72 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2940.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1620.64 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 3036.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2151.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3170.14 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2940.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3173.55 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3173.55 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2748.27 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2748.52 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2738.8 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2256.97 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2748.52 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2024.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2168.72 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2833.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2536.5 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3170.14 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2256.97 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2738.8 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1620.64 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2536.5 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Chief Joseph-Snohomish #3 or #4 operating at 230kV (COV-CRES BYP @ COV)
G0 | 287.87 | 648.17 | 395.08 | 1762.45 | 2024.23
G1 | 405.72 | 766.06 | 510.84 | 1896.66 | 2151.08 | Season/Year: | WINTER 2009
G2 | 507.74 | 883.08 | 628.06 | 1996.43 | 2238.94 | Direction: | North-to-South (NS)
G3 | 1299.57 | 1588.19 | 1331.39 | 2593.18 | 2833.01 | Case Loads: | Heavy Loads
G4 | 1418.23 | 1712.04 | 1451.19 | 2711.88 | 2940.81 | Outage: | 013
G5 | 1529.8 | 1829.62 | 1535.94 | 2816.07 | 3036.1 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3090.72 | 3342.15 | 3086.84 | 3237.43 | 3170.14 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3193.82 | 3361.73 | 3179.02 | 3240.02 | 3173.55 | Study Person: | FRP9899
G8 | 3323.08 | 3516.86 | 3259.88 | 3254.78 | 2748.27 | Source: | 013WINTER09v2NSH
G9 | 3040.18 | 3093.62 | 3030.77 | 2820.05 | 2738.8
G10 | 3196.13 | 3093.16 | 3040.33 | 2828.72 | 2748.52
G11 | 2922.64 | 3108.76 | 3051.49 | 2851.94 | 2168.72
G12 | 3037.86 | 2949.24 | 2886.57 | 2652.77 | 2536.5
G13 | 3050.44 | 2959.35 | 2898.42 | 2686.58 | 2256.97
G14 | 2443.62 | 2813.18 | 2844.43 | 2480.05 | 1620.64
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 013 | Chief Joseph-Snohomish #3 or #4 operating at 230kV (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6464.6593 | 287.87 | 405.72 | 507.74 | 1299.57 | 1418.23 | 1529.8 | 3090.72 | 3193.82 | 3323.08 | 3040.18 | 3196.13 | 2922.64 | 3037.86 | 3050.44 | 2443.62
35F | 6150.4293 | 648.17 | 766.06 | 883.08 | 1588.19 | 1712.04 | 1829.62 | 3342.15 | 3361.73 | 3516.86 | 3093.62 | 3093.16 | 3108.76 | 2949.24 | 2959.35 | 2813.18
45F | 5867.504 | 395.08 | 510.84 | 628.06 | 1331.39 | 1451.19 | 1535.94 | 3086.84 | 3179.02 | 3259.88 | 3030.77 | 3040.33 | 3051.49 | 2886.57 | 2898.42 | 2844.43
60F | 4840.6613 | 1762.45 | 1896.66 | 1996.43 | 2593.18 | 2711.88 | 2816.07 | 3237.43 | 3240.02 | 3254.78 | 2820.05 | 2828.72 | 2851.94 | 2652.77 | 2686.58 | 2480.05
70F | 4511.2333 | 2024.23 | 2151.08 | 2238.94 | 2833.01 | 2940.81 | 3036.1 | 3170.14 | 3173.55 | 2748.27 | 2738.8 | 2748.52 | 2168.72 | 2536.5 | 2256.97 | 1620.64

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 286.79 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 473.28 | 473.21 | 6410.13 | 287.87 | -30.12 | FULL
G1 | 404.87 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 473.51 | 473.44 | 6350.69 | 405.72 | 70.35 | FULL
G2 | 507.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 473.59 | 473.5 | 6374.59 | 507.74 | 161.09 | FULL
G3 | 1301.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 484.86 | 484.66 | 6429.13 | 1299.57 | 612.67 | FULL
G4 | 1420.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 484.83 | 484.82 | 6373.46 | 1418.23 | 717.52 | FULL
G5 | 1533.94 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 485.26 | 485.3 | 6399.87 | 1529.8 | 811.53 | FULL
G6 | 3105.26 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 30.81 | 1308.03 | 1300.83 | 6514.17 | 3090.72 | 1715.2 | FULL
G7 | 3209.59 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 490.79 | 490.76 | 6464.08 | 3193.82 | 1817.31 | FULL
G8 | 3340.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 490.54 | 490.69 | 6496.48 | 3323.08 | 1925.25 | FULL
G9 | 3055.54 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 30.81 | 1396.47 | 1334.45 | 6549.22 | 3040.18 | 1902.75 | FULL
G10 | 3212.37 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -513.65 | -513.01 | 6499.75 | 3196.13 | 2020.8 | FULL
G11 | 2937.82 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | 3.06 | 458.07 | 458 | 6509.27 | 2922.64 | 1896.06 | FULL
G12 | 3052.62 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -512.88 | -512.29 | 6574.54 | 3037.86 | 2051.83 | FULL
G13 | 3064.18 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -513.33 | -512.76 | 6519.51 | 3050.44 | 2090.49 | FULL
G14 | 2451.94 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 3.06 | 458.52 | 458.6 | 6505 | 2443.62 | 1776.14 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 647.71 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 469.03 | 468.81 | 6089.08 | 648.17 | 214.22 | FULL
G1 | 765.63 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 469.38 | 469.17 | 6031.99 | 766.06 | 314 | FULL
G2 | 881.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 469.66 | 469.45 | 6056.69 | 883.08 | 413.69 | FULL
G3 | 1592.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 477.38 | 477.34 | 6113.52 | 1588.19 | 811.44 | FULL
G4 | 1717.33 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 477.61 | 477.78 | 6059.46 | 1712.04 | 914.87 | FULL
G5 | 1835.73 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 478.16 | 478.28 | 6087.6 | 1829.62 | 1013.46 | FULL
G6 | 3359.01 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 481.91 | 481.88 | 6207.44 | 3342.15 | 1911.09 | FULL
G7 | 3381.14 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 30.81 | 1325.93 | 1334.59 | 6155.7 | 3361.73 | 1941.64 | CTG_FAIL_IN_FULL
G8 | 3536.7 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -490.14 | -489.94 | 6191.05 | 3516.86 | 2069.84 | FULL
G9 | 3109.2 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -501.43 | -500.67 | 6228.72 | 3093.62 | 1974.03 | FULL
G10 | 3109.12 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -500.99 | -500.12 | 6175.09 | 3093.16 | 1990.63 | FULL
G11 | 3124.35 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -499.36 | -498.67 | 6202.84 | 3108.76 | 2044.9 | FULL
G12 | 2962.77 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -502.04 | -501.66 | 6249.72 | 2949.24 | 2033.21 | FULL
G13 | 2973.16 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -502.06 | -501.48 | 6196.12 | 2959.35 | 2070.42 | FULL
G14 | 2825.91 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 3.06 | 460.08 | 460.11 | 6211.42 | 2813.18 | 2014.28 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 394.02 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 434.9 | 434.79 | 5806.69 | 395.08 | 85.39 | FULL
G1 | 509.94 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 435.12 | 435.02 | 5748.91 | 510.84 | 185.28 | FULL
G2 | 625.79 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 436.05 | 435.92 | 5773.45 | 628.06 | 284.82 | FULL
G3 | 1334.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 442.5 | 442.61 | 5828.35 | 1331.39 | 683.22 | FULL
G4 | 1455.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 443.02 | 443.13 | 5774.18 | 1451.19 | 784.04 | FULL
G5 | 1539.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 442.05 | 442.16 | 5800.59 | 1535.94 | 864.2 | FULL
G6 | 3102.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 447.22 | 447.19 | 5916.84 | 3086.84 | 1774.12 | FULL
G7 | 3195.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 446.42 | 446.39 | 5866.65 | 3179.02 | 1855.76 | FULL
G8 | 3276.61 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 446.02 | 445.97 | 5898.93 | 3259.88 | 1938.01 | FULL
G9 | 3044.4 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -493.21 | -492.79 | 5949.77 | 3030.77 | 1932.39 | FULL
G10 | 3054.13 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -492.63 | -492.39 | 5895.89 | 3040.33 | 1969.85 | FULL
G11 | 3066.25 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -492.34 | -491.89 | 5923.77 | 3051.49 | 2007.46 | FULL
G12 | 2899.27 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -492.18 | -492.52 | 5971.09 | 2886.57 | 2025.63 | FULL
G13 | 2911.3 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -494.25 | -493.52 | 5917.77 | 2898.42 | 2051.61 | FULL
G14 | 2856.74 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 3.06 | 459.74 | 459.77 | 5939.68 | 2844.43 | 2056.42 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1768.37 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 443.09 | 443.23 | 4787.33 | 1762.45 | 983.96 | FULL
G1 | 1901.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 444.47 | 444.57 | 4737.07 | 1896.66 | 1091.61 | FULL
G2 | 2003.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 444.54 | 444.52 | 4766.79 | 1996.43 | 1180.25 | FULL
G3 | 2604.52 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 447.02 | 447.08 | 4831.12 | 2593.18 | 1498.31 | FULL
G4 | 2724.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 447.32 | 447.35 | 4782.11 | 2711.88 | 1604.6 | FULL
G5 | 2828.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 447.71 | 447.8 | 4815.71 | 2816.07 | 1695.23 | FULL
G6 | 3254.59 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -471.67 | -471.97 | 4886.44 | 3237.43 | 1967.28 | FULL
G7 | 3257.23 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -470.69 | -471.1 | 4835.8 | 3240.02 | 1993.37 | FULL
G8 | 3272.05 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -471.25 | -471.73 | 4864.19 | 3254.78 | 2040.99 | FULL
G9 | 2831.99 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.66 | -476.95 | -476.16 | 4899 | 2820.05 | 1943.65 | FULL
G10 | 2841.04 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.66 | -476.98 | -476.15 | 4847.54 | 2828.72 | 1966.92 | FULL
G11 | 2864.28 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.66 | -478.48 | -477.58 | 4876.36 | 2851.94 | 2032.41 | FULL
G12 | 2662.75 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -12.79 | -459.78 | -459.76 | 4922.1 | 2652.77 | 2001.6 | FULL
G13 | 2695.92 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.66 | -477.13 | -476.41 | 4872.07 | 2686.58 | 2038.34 | FULL
G14 | 2489.34 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.59 | -190.94 | -190.87 | 4886.29 | 2480.05 | 1959 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2030.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 444.9 | 444.98 | 4474.02 | 2024.23 | 1163.93 | FULL
G1 | 2158.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 445.62 | 445.78 | 4424.41 | 2151.08 | 1254.79 | FULL
G2 | 2247.75 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 445.07 | 445.17 | 4456.06 | 2238.94 | 1335.11 | FULL
G3 | 2845.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 447.11 | 447.42 | 4520.44 | 2833.01 | 1669.15 | FULL
G4 | 2953.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 447.89 | 447.89 | 4473.15 | 2940.81 | 1761.14 | FULL
G5 | 3049.95 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.52 | 447.66 | 447.74 | 4507.2 | 3036.1 | 1844.08 | FULL
G6 | 3186.4 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.66 | -461.69 | -460.76 | 4561.15 | 3170.14 | 1962.12 | FULL
G7 | 3189.58 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.66 | -460.38 | -459.41 | 4509.37 | 3173.55 | 1998.97 | FULL
G8 | 2759.72 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.6 | -173.51 | -173.45 | 4509.57 | 2748.27 | 1799.25 | FULL
G9 | 2750.45 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.66 | -462.46 | -461.61 | 4572.39 | 2738.8 | 1919.36 | FULL
G10 | 2760.18 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.66 | -461.05 | -460.25 | 4520.45 | 2748.52 | 1965.06 | FULL
G11 | 2176.58 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.6 | -173.99 | -173.98 | 4512.17 | 2168.72 | 1680.83 | FULL
G12 | 2545.91 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -12.79 | -447.39 | -447.68 | 4593.23 | 2536.5 | 1959.68 | FULL
G13 | 2265.12 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.6 | -173.58 | -173.57 | 4521.76 | 2256.97 | 1848.37 | FULL
G14 | 1624.77 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.6 | -173.43 | -173.43 | 4513.13 | 1620.64 | 1521.78 | FULL
013WINTER09v2NSH