## 25F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 049
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6648.1447
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 326.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 537.48 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 439.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1547.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 537.48 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2992.73 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 140 | 1328.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2304.93 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1433.52 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1813.17 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1547.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 439.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3101.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1433.52 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3199.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3199.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2992.73 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2946.39 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 140 | 2883.96 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2331.69 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 460 | 2946.39 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 326.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2304.93 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1328.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 3041.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3101.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2331.69 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2883.96 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1400 | 775 | 1813.17 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 3041.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 049
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6323.296
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 682.67 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 908.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 798.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1891.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 908.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3243.16 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 140 | 1610.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2391.13 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1748.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1959.83 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1891.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 798.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3364.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1748.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3422.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3422.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3243.16 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3097.65 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3095.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2812.4 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 460 | 3097.65 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 682.67 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2391.13 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1610.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2952.98 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3364.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2812.4 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3095.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1959.83 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2952.98 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 049
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6038.4607
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 430.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 654.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 540.46 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1572.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 654.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3149.25 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1358.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2664.48 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1462.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2140.24 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 1572.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 540.46 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3089.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1462.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3181.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3181.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3149.25 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3010.64 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 3034.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2600.69 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 3010.64 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 430.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2664.48 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1358.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2892.45 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3089.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2600.69 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3034.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2140.24 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2892.45 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 049
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4942.6293
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1779.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1888.7 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1902.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1720.32 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1888.7 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1452.21 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2403.65 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 972.44 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 2050.26 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 557.33 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1720.32 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 1902.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2135.23 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2050.26 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 1785.25 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1785.25 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1452.21 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1311 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1665.07 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 902.2 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 1311 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1779.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 972.44 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2403.65 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1257.7 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2135.23 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 902.2 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1665.07 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 557.33 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1257.7 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 049
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4594.7053
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1621.39 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 942.77 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1275.28 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 778.63 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 942.77 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 506.79 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1455.84 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 26.86 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 1111.56 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -370.72 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 778.63 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1275.28 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 1190.39 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1111.56 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 849.1 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 849.1 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 506.79 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 362.05 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 712.44 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | -44.8 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 362.05 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1621.39 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 26.86 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1455.84 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 306.14 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1190.39 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | -44.8 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 712.44 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | -370.72 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 306.14 | BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
G0 | 326.01 | 682.67 | 430.27 | 1779.88 | 1621.39
G1 | 439.74 | 798.11 | 540.46 | 1902.16 | 1275.28 | Season/Year: | WINTER 2009
G2 | 537.48 | 908.95 | 654.08 | 1888.7 | 942.77 | Direction: | North-to-South (NS)
G3 | 1328.82 | 1610.78 | 1358.27 | 2403.65 | 1455.84 | Case Loads: | Heavy Loads
G4 | 1433.52 | 1748.6 | 1462.87 | 2050.26 | 1111.56 | Outage: | 049
G5 | 1547.89 | 1891.79 | 1572.54 | 1720.32 | 778.63 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3101.9 | 3364.81 | 3089.45 | 2135.23 | 1190.39 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3199.96 | 3422.19 | 3181.77 | 1785.25 | 849.1 | Study Person: | JGO7470
G8 | 2992.73 | 3243.16 | 3149.25 | 1452.21 | 506.79 | Source: | 049WINTER09v2NSH
G9 | 2883.96 | 3095.68 | 3034.06 | 1665.07 | 712.44
G10 | 2946.39 | 3097.65 | 3010.64 | 1311 | 362.05
G11 | 2304.93 | 2391.13 | 2664.48 | 972.44 | 26.86
G12 | 3041.42 | 2952.98 | 2892.45 | 1257.7 | 306.14
G13 | 2331.69 | 2812.4 | 2600.69 | 902.2 | -44.8
G14 | 1813.17 | 1959.83 | 2140.24 | 557.33 | -370.72
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 049 | Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6648.1447 | 326.01 | 439.74 | 537.48 | 1328.82 | 1433.52 | 1547.89 | 3101.9 | 3199.96 | 2992.73 | 2883.96 | 2946.39 | 2304.93 | 3041.42 | 2331.69 | 1813.17
35F | 6323.296 | 682.67 | 798.11 | 908.95 | 1610.78 | 1748.6 | 1891.79 | 3364.81 | 3422.19 | 3243.16 | 3095.68 | 3097.65 | 2391.13 | 2952.98 | 2812.4 | 1959.83
45F | 6038.4607 | 430.27 | 540.46 | 654.08 | 1358.27 | 1462.87 | 1572.54 | 3089.45 | 3181.77 | 3149.25 | 3034.06 | 3010.64 | 2664.48 | 2892.45 | 2600.69 | 2140.24
60F | 4942.6293 | 1779.88 | 1902.16 | 1888.7 | 2403.65 | 2050.26 | 1720.32 | 2135.23 | 1785.25 | 1452.21 | 1665.07 | 1311 | 972.44 | 1257.7 | 902.2 | 557.33
70F | 4594.7053 | 1621.39 | 1275.28 | 942.77 | 1455.84 | 1111.56 | 778.63 | 1190.39 | 849.1 | 506.79 | 712.44 | 362.05 | 26.86 | 306.14 | -44.8 | -370.72

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 323.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 473.17 | 473.23 | 6659.29 | 326.01 | -16.49 | FULL
G1 | 438.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 473.73 | 473.67 | 6589.62 | 439.74 | 81.91 | FULL
G2 | 539.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 473.8 | 473.73 | 6601.39 | 537.48 | 170.38 | FULL
G3 | 1330.6 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 484.99 | 484.8 | 6657.23 | 1328.82 | 620.16 | FULL
G4 | 1436.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 485.02 | 484.82 | 6589.4 | 1433.52 | 703.22 | FULL
G5 | 1552.36 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 485.5 | 485.33 | 6603.54 | 1547.89 | 799.98 | FULL
G6 | 3116.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 490.91 | 491.1 | 6701.46 | 3101.9 | 1709.38 | FULL
G7 | 3215.82 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 490.66 | 490.62 | 6639.12 | 3199.96 | 1808.41 | FULL
G8 | 3006.28 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.97 | 459.95 | 460.02 | 6645.01 | 2992.73 | 1727.58 | FULL
G9 | 2898.17 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 31.24 | 1327.93 | 1258.01 | 6722.74 | 2883.96 | 1802.91 | FULL
G10 | 2960.11 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.97 | 458.93 | 458.97 | 6650.09 | 2946.39 | 1867.57 | FULL
G11 | 2314.92 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.97 | 459.26 | 459.31 | 6640.92 | 2304.93 | 1550.63 | FULL
G12 | 3055.25 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -512.6 | -512.02 | 6739.97 | 3041.42 | 2041.82 | FULL
G13 | 2340.34 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.97 | 458.07 | 458 | 6642.59 | 2331.69 | 1691.16 | FULL
G14 | 1817.85 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.97 | 459.27 | 459.34 | 6639.8 | 1813.17 | 1428.12 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 683.86 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 469.34 | 469.08 | 6325.14 | 682.67 | 226.05 | FULL
G1 | 796.73 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 469.58 | 469.37 | 6255.61 | 798.11 | 324.39 | FULL
G2 | 907.46 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 469.81 | 469.61 | 6268.39 | 908.95 | 419.73 | FULL
G3 | 1615.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 477.3 | 477.51 | 6327.67 | 1610.78 | 815.09 | FULL
G4 | 1754.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 478.53 | 478.6 | 6262 | 1748.6 | 917.65 | FULL
G5 | 1897.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 480.01 | 480.08 | 6278.19 | 1891.79 | 1035.17 | FULL
G6 | 3383.56 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 481.51 | 481.46 | 6382.66 | 3364.81 | 1911.97 | FULL
G7 | 3442.03 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 479.94 | 479.84 | 6319.92 | 3422.19 | 1962.38 | FULL
G8 | 3259.34 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.97 | 460.38 | 460.45 | 6327.22 | 3243.16 | 1901.3 | FULL
G9 | 3111.49 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -500.95 | -500.2 | 6395.96 | 3095.68 | 1962.49 | FULL
G10 | 3112.33 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -500.99 | -500.14 | 6328.98 | 3097.65 | 1988.83 | FULL
G11 | 2399.79 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.97 | 458.23 | 458.21 | 6315.33 | 2391.13 | 1632.01 | FULL
G12 | 2966.81 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -502.78 | -502.4 | 6408.67 | 2952.98 | 2033.58 | FULL
G13 | 2825.29 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.97 | 460.15 | 460.21 | 6336.44 | 2812.4 | 1981.72 | FULL
G14 | 1965.87 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.97 | 458.9 | 458.96 | 6317.26 | 1959.83 | 1547.17 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 427.65 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 435.03 | 434.94 | 6041.01 | 430.27 | 98.9 | FULL
G1 | 539.43 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 435.28 | 435.19 | 5971.32 | 540.46 | 194.84 | FULL
G2 | 652.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 436.28 | 436.09 | 5983.84 | 654.08 | 291.6 | FULL
G3 | 1360.16 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.57 | 442.76 | 6041.32 | 1358.27 | 689.81 | FULL
G4 | 1465.49 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.56 | 442.67 | 5974.02 | 1462.87 | 773.54 | FULL
G5 | 1575.82 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 443.18 | 443.33 | 5989.96 | 1572.54 | 866.71 | FULL
G6 | 3105.47 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 446.76 | 446.83 | 6088.91 | 3089.45 | 1763.5 | FULL
G7 | 3198.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 446.44 | 446.6 | 6026.29 | 3181.77 | 1844.74 | FULL
G8 | 3165.48 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 672.42 | 672.37 | 6042 | 3149.25 | 1864.81 | FULL
G9 | 3047.75 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -492.97 | -492.56 | 6111.58 | 3034.06 | 1921.77 | FULL
G10 | 3024.79 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 672.34 | 672.3 | 6045.79 | 3010.64 | 1940.19 | FULL
G11 | 2675.2 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.97 | 459.77 | 459.8 | 6044.73 | 2664.48 | 1789.53 | FULL
G12 | 2904.28 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -492.9 | -492.16 | 6124.81 | 2892.45 | 2005.19 | FULL
G13 | 2611.5 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 672.5 | 672.46 | 6048.67 | 2600.69 | 1880.2 | FULL
G14 | 2147.16 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.53 | -199.91 | -199.87 | 6042.66 | 2140.24 | 1652 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1784.01 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 443.37 | 443.45 | 4968.48 | 1779.88 | 986.72 | FULL
G1 | 1907.37 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 444.12 | 444.18 | 4904.65 | 1902.16 | 1085.4 | FULL
G2 | 1893.9 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 641.13 | 641.06 | 4921.12 | 1888.7 | 1108.92 | FULL
G3 | 2412.36 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 640.49 | 640.46 | 4987.37 | 2403.65 | 1382.48 | FULL
G4 | 2058.05 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 640.78 | 640.76 | 4912.73 | 2050.26 | 1220.58 | FULL
G5 | 1725.44 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 640.97 | 640.96 | 4921.12 | 1720.32 | 1068.65 | FULL
G6 | 2143.4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 640.67 | 640.65 | 4988.51 | 2135.23 | 1350.42 | FULL
G7 | 1789.88 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 640.81 | 640.73 | 4913.45 | 1785.25 | 1187.96 | FULL
G8 | 1455.63 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 641.03 | 641.02 | 4921.76 | 1452.21 | 1034.58 | FULL
G9 | 1668.8 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 640.75 | 640.73 | 4994.48 | 1665.07 | 1289.92 | FULL
G10 | 1313.57 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 640.98 | 640.97 | 4919.39 | 1311 | 1126.81 | FULL
G11 | 973.07 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 641.09 | 641.08 | 4927.92 | 972.44 | 970.6 | FULL
G12 | 1258.13 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 640.85 | 640.85 | 4999.43 | 1257.7 | 1216.48 | FULL
G13 | 904 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 641.05 | 641.03 | 4925.16 | 902.2 | 1051.05 | FULL
G14 | 556.54 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 641.13 | 641.07 | 4933.87 | 557.33 | 892.25 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1626.1 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.46 | 618.45 | 4634.39 | 1621.39 | 927.26 | FULL
G1 | 1277.63 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.66 | 618.65 | 4562.81 | 1275.28 | 765.08 | FULL
G2 | 944.66 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.72 | 618.71 | 4574.71 | 942.77 | 609.28 | FULL
G3 | 1459.78 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.57 | 618.54 | 4633.11 | 1455.84 | 897.76 | FULL
G4 | 1114.24 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.58 | 618.49 | 4562.22 | 1111.56 | 729.57 | FULL
G5 | 777.54 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.59 | 618.59 | 4574.11 | 778.63 | 574.28 | FULL
G6 | 1193.53 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.39 | 618.37 | 4634.26 | 1190.39 | 858.91 | FULL
G7 | 849.97 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.85 | 618.84 | 4562.94 | 849.1 | 706.53 | FULL
G8 | 505.02 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.87 | 618.85 | 4574.71 | 506.79 | 545.62 | FULL
G9 | 713.71 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.74 | 618.72 | 4640.67 | 712.44 | 802.06 | FULL
G10 | 360.76 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.81 | 618.84 | 4569.79 | 362.05 | 637.39 | FULL
G11 | 25.32 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.92 | 618.91 | 4581.9 | 26.86 | 479.8 | FULL
G12 | 304.31 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.76 | 618.79 | 4647.35 | 306.14 | 726.22 | FULL
G13 | -46.27 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.91 | 618.9 | 4577.17 | -44.8 | 561.53 | FULL
G14 | -372.03 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | BFR: Covington 230kV West Bus | 4.31 | 618.97 | 618.96 | 4590.44 | -370.72 | 409.92 | FULL
049WINTER09v2NSH