Kyiv, Ukraine 						February 7, 2008

### SUBJECT:  Solicitation Number SOUP300-08-Q-0003 for Installation of Contractor-Furnished

### 100KVA Standby Diesel Generator Set(Single Operation)With New ATS at U.S. Consulate Building Kyiv, Ukraine.

The Embassy of the United States of America invites you to submit a proposal for Design/Construction services of US Government Property located at  6 Pimonenko St, in Kyiv, Ukraine.  Construction shall consist of mostly exterior construction and installation works.

If you are interested in submitting a proposal on this project, read the instructions in Section L of the attached Request for Proposals (RFP).

If you intend to submit a proposal, you should thoroughly examine all documents contained in the contract solicitation package and arrange for a personal inspection of the project site by a representative from your company.  The Embassy intends to conduct a a site visit , and all prospective offerors who have received a solicitation package will be invited to attend.  The site visit will be held at 6 Pimonenko Street on February  20, 2008 in 11:00 a.m.  Submit any questions you may have concerning the solicitation documents in writing by February 25, 2008 so that a response can be provided at this meeting.

Your proposal must be submitted in a sealed envelope marked "Proposal Enclosed" to the Maura Pellet, Contracting Officer at Artem Center located at 4 Glubochytska Street on or before 17:00 p.m. on March 5, 2008.  No proposal will be accepted after this time.

Complete Part II of the Standard Form 1442, including all blank spaces, and have the form signed by an authorized representative of your company, or the proposal may be considered unacceptable and may be rejected.

In order for a proposal to be considered, you must also complete and submit the following:

1.  Sections B and Attachment 4, Proposal Breakdown by                 Divisions;

- Section K, Representations and Certifications;

3.  Bar Chart illustrating sequence of work to be performed;

4.  Additional information as required in Section L.

The contract will be a firm fixed price contract, with no adjustment for any escalation in costs or prices of labor or materials.  Each offeror will be responsible for determining the amount of labor and materials that will be required to complete the project, and for pricing its proposal accordingly.

Please be advised that each offeror is responsible for furnishing complete information to its subcontractor and suppliers, such as details and quantities required by the drawings and specifications.  Subcontractors and suppliers should not be referred to the Embassy or the Architect for determining the amount or quantities of materials required.

The construction/installation completion time is 90 calendar days, commencing on March, 2008.  In the event of an unauthorized or unexcused delay in completing the project, liquidated damages in the amount of $140.00 per calendar day will be assessed until substantial completion of the project is achieved.

The Contracting Officer reserves the right to reject any and all proposals and to waive any informality in proposals received.  In addition, the Embassy reserves the right to establish a competitive range of one or more offerors and to conduct further negotiations concerning price and other terms before awarding the contract, or to award without discussions.

Please direct any questions regarding this solicitation Olena Stavnycha by letter or by telephone 490-4113, fax 490-4085 during regular business hours.

Sincerely,

Maura Pellet

Contracting Officer

American Embassy Kyiv, Ukraine

TABLE OF CONTENTS

SF 18 or SF 1442 cover sheet

A.   Price

B.   Scope of Work

C.  Packaging and Marking

D.  Inspection and Acceptance

E.  Deliveries/Performance

F.  Administrative Data

G.  Special Requirements

H.  Clauses

I.    List of Attachments

J.   Quotation Information

K.  Evaluation Criteria

L.  Representations, Certifications, and other Statements of Offerors or Quoters

Attachment 1:  Sample Bank Letter of Guarantee

Attachment #2: BREAKDOWN OF PRICE BY DIVISIONS OF SPECIFICATIONS

| SOLICITATION, OFFER, AND AWARD (Construction) | 1. SOLICITATION NO. SOUP300-08-Q-0003 | 2. TYPE OF SOLICITATION SEALED BID (IFB) X NEGOTIATED (RFP) | 3. DATE ISSUED 02/07/08 | PAGE OF PAGES1 2 |
| --- | --- | --- | --- | --- |
| IMPORTANT - The “offer” section on the reverse must be fully completed by offeror. |
| 4. CONTRACT NO. | 5. REQUISITION/PURCHASE REQUEST NO. | 6. PROJECT NO. XJDO0084 |
| 7. ISSUED BY CODE |  | 8. ADDRESS OFFER TO |
| American Embassy Kyiv, Ukraine 4 Glubochytska St. |  |
| 9. FOR INFORMATION CALL: | A. NAME Olena Stavnycha | TELEPHONE NO. 490-41-13, FAX. 490-40-85 |
| SOLICITATION |
| NOTE: In sealed bid solicitations “offer” and “offeror” mean “bid” and “bidder.” |
| THE GOVERNMENT REQUIRES PERFORMANCE OF THE WORK DESCRIBED IN THESE DOCUMENTS (Title, identifying no., date): SF 18 or SF 1442 cover sheet A. Price B. Scope of Work C. Packaging and Marking D. Inspection and Acceptance E. Deliveries/Performance F. Administrative Data G. Special Requirements H. Clauses I. List of Attachments J. Quotation Information K. Evaluation Criteria L. Representations, Certifications, and other Statements of Offerors or Quoters Attachments #1, 2 |
| 11. The Contractor shall begin performance within _10_calendar days and complete it within _90 calendar days after receiving award, X notice to proceed. This performance period is __ mandatory, negotiable. |
| 12A. THE CONTRACTOR MUST FURNISH ANY REQUIRED PERFORMANCE AND PAYMENT BONDS? (If “YES,” indicate within how many calendar days after award in Item 12B.) YES YES NO | 12B. CALENDAR DAYS 10 days |
| 13. ADDITIONAL SOLICITATION REQUIREMENTS: A. Sealed offers in original and ___ copies to perform the work required are due at the place specified in Item 8 by -- local time (hour) local time, (date). Sealed envelopes containing offers shall be marked to show the offeror’s name and address, the solicitation number, and the date and time offers are due. B. An offer guarantee is, X is not required. C. All offers are subject to the (1) work requirements, and (2) other provisions and clauses incorporated in the solicitation in full text or by reference. D. Offers providing less than _60__ calendar days for Government acceptance after the date offers are due will not be considered and will be rejected. |

NSN 7540-01-155-3212	1442-101		STANDARD FORM 1442 (REV. 4-85) Prescribed by GSA 								FAR (48 CFR) 53.236-1(e)

| OFFER (Must be fully completed by offeror) |
| --- |
|  | 15. TELEPHONE NO. (Include area code) |
|  | 16. REMITTANCE ADDRESS (Include only if different than Item 14) |
| CODE FACILITY CODE |  |
| 17. The offeror agrees to perform the work at the prices specified below in strict accordance with the terms of this solicitation, if this offer is accepted by the Government within 90 calendar days after the date offers are due. AMOUNTS in USD |
| 18. The offeror agrees to furnish any required performance and payment bonds. |
| 19. ACKNOWLEDGMENT OF AMENDMENTS The offeror acknowledges receipt of amendments to the solicitation -- give number and date of each |
| AAAMENDMENT NO. |  |  |  |  |  |  |  |  |  |  |
| DATE |  |  |  |  |  |  |  |  |  |  |
| 20A. NAME AND TITLE OF PERSON AUTHORIZED TO SIGN OFFER (Type or print) | 20B. SIGNATURE | 20C. OFFER DATE |
| AWARD (To be completed by Government) |
| 21. ITEMS ACCEPTED: as specified in the SOUP300-04-R-0005 |
| 22. AMOUNT | 23. ACCOUNTING AND APPROPRIATION DATA |
| 24. SUBMIT INVOICES TO ADDRESS SHOWN IN ITEM 7 (2 copies) | ITEM | 25. OTHER THAN FULL AND OPEN COMPETITION PURSUANT TO 10 U.S.C. 2304(c)( ) 41 U.S.C. 253(c)( ) |
| 26. ADMINISTERED BY CODE |  | 27. PAYMENT WILL BE MADE BY |
| US Embassy Kyiv, Ukraine |  | Electronic Bank Transfer |
| CONTRACTING OFFICER WILL COMPLETE ITEM 28 OR 29 AS APPLICABLE |
| 28. NEGOTIATED AGREEMENT (Contractor is required to sign this document and return __2__ copies to issuing office.) A contractor agrees to furnish and deliver all items or performs all work, requisitions identified on this form and any continuation sheets for the consideration slated in this contract. The rights and obligations of the parties to this contract shall be governed by (a) this contract award, (b) the solicitation, and (c) the clauses, representations, certifications, and specifications or incorporated by reference in or attached to this contract. | 29. AWARD (Contractor is not required to sign this document.) Your offer on this solicitation is hereby accepted as to the items listed. This award consummates the contract, which consists of (a) the Government solicitation and your offer, and (b) this contract award. No further contractual document is necessary. |
| 30A. NAME AND TITLE OF CONTRACTOR OR PERSON AUTHORIZED TO SIGN (Type or print) | 31A. NAME OF CONTRACTING OFFICER Maura Pellet |
| 30B. SIGNATURE | 30C. DATE | 31B. UNITED STATES OF AMERICA BY | 31C. AWARD DATE |

Computer Generated		STANDARD FORM 1442 BACK (REV. 4-85)

REQUEST FOR QUOTATIONS - CONSTRUCTION

- A.     PRICE

The contractor shall complete all work, including furnishing all labor, material, equipment and services required under this purchase order for the following firm fixed price and within the time specified.  This price shall include all labor, materials, overhead and profit.

__________________________  Total Price

### B.	SCOPE OF WORK FOR:

Installation of Contractor-Furnished and Installed 100KVA Standby Diesel Generator Set (Single Operation) With New ATS U.S. Consulate Building          Kyiv, Ukraine

1.0	PROJECT DESCRIPTION

This project provides for the installation of a new 100KVA diesel engine generator and associated automatic transfer switch (ATS).  The new generator is to provide emergency backup power for the U.S. Consulate building located at 6, Pymonenka Street in Kyiv.

There is currently no back up power for this compound, but it is desired that all Consular building loads be placed under automatic generator power when utility power is lost.  The new generator shall be a diesel generator set with a standby rating of 100KVA or higher, weatherproof and sound limiting housing enclosure, 380Y/220 nominal voltage, 3 phase, 50 hertz, complete with automatic transfer switch, and is to be interconnected to the Consulate building’s electrical distribution system.

Included in this effort is the installation of a new 2,000L or larger double-walled fuel tank inside of the enclosure, control wiring, properly sized load wires with conduit or cable tray, replacement of two fuses and a circuit breaker, and other miscellaneous works identified below.  Further, this effort includes the restoration of all affected parts of the facility to acceptable condition.

- SCOPE

This is a level of effort wherein the contractor shall provide equipment, labor, materials, and installation drawing plans necessary to install a complete new operational generator power system including ATS.  The effort includes the installation of generator, weatherproof and critical grade sound limiting enclosure, automatic transfer switch, fuel tank, feeder circuits, modifications to the existing building electrical distribution system, connection to the existing electrical distribution system, control circuit, equipment foundation, and fuel lines.  The contractor must also provide testing and coordination for a safe and fully operational generator power system.

- PROJECT REQUIREMENTS

3.1	General Requirements:  The requirements in this Scope of Work serve as direction to the Contractor in the development, execution and delivery of a completely operational and automatic standby generator system.  The Contractor shall review this Scope of Work and be familiar with the project requirements.  Questions and needed clarifications shall be submitted to the Contracting Officer (CO) for answers and resolution.  A thorough knowledge of the project is required to achieve a substantive quality finished product. Any exceptions to the SOW must be clearly stated in the Contractor’s proposal as exceptions.

3.2	Contractor Furnished-Contractor Installed Material:  The contractor shall furnish the generator set, automatic transfer switch, and all other equipment and materials required under this SOW.

3.3	Changes to the Scope of Work:  Any changes to this Scope of Work shall have the written approval of the Contracting Officer or his/her representative, and all desired changes to this Scope shall be directed to the same.

3.4	Contract Price Changes:  No changes will be made in this fixed price contract due to price fluctuations for materials or exchange rates.  The contractor with the Lowest Price Technically Acceptable (LPTA) bid may then be selected to implement the project.  No bidder may be selected at the Government’s option.

3.5	Security Clearance: No security clearance is required in the performance of this work.

- TECHNICAL REQUIREMENTS

  - Diesel Generator Set:  Contractor shall install a contractor furnished standby duty diesel generator set with associated controls to provide a fully automatic system to support the Consular Building’s total connected load.  The new generator set shall be installed on the opposite site of the building as the utility fuse box and adjacent to the Maintenance Shop circuit breaker on the Consular building exterior wall.  The contractor shall be thoroughly familiar with the generator set manufacturer’s installation requirements.  The generator technical requirements shall be as stated in Attachment 1 of the SOW.

  - Automatic Transfer Switch (ATS): Contractor shall install a contractor furnished automatic transfer switch that will connect the Consular Building loads to either the City power if available and of acceptable quality, or to the generator set when adequate quality utility power is not available.  Provide the required control wiring between the ATS and the generator set for automatic starting and stopping of the generator set. The contractor shall be thoroughly familiar with the ATS manufacturer’s installation requirements.  The ATS technical requirements shall be as stated in Attachment 1 of the SOW.

4.3 	Feeders in Conduit or Cable Tray:  Contractor shall provide a final electrical distribution system as shown on Attachment 3 “Proposed Electrical One-Line.”  The contractor shall verify that stated wire sizes in Attachment 3 meet the US National Electric Code and all local codes.  Wiring shall be copper, insulated with moisture and heat resistant thermoplastic rated for 75 degree C or higher operation.  The distance of run shall be verified by the contractor.  The wiring shall all be protected with properly-sized (per US National Electrical Code) galvanized conduit or cable tray.  Conduits or cable tray shall be run along exterior walls or through the Consular Building attic space.  Conduit from the generator enclosure to the building wall shall be in schedule 40 or schedule 80 PVC buried at a depth of 48 inches or deeper.

  - Utility Fuses:  The load-side fuses in the utility fuse box shall be replaced with 200A fuses as shown on Attachment 3.  The fuse box door shall be permanently repaired to function as originally intended.  The contractor is responsible with coordinating with the local electric utility if needed to accomplish this.

  - Auxiliary Equipment/Circuits: Contractor shall make proper electrical connections as needed to supply power to the battery charger, fuel pumps, generator strip heater, engine jacket water heater, lube oil heater, and other components requiring power.

  - Panel MDP Alteration: The main breaker serving the building panel MDP shall be downsized to 200A.

  - Electrical System Grounding:  Contractor shall provide a driven copper clad ground rod (19mm diameter) near the generator location with bare copper wire 95mm2 (3/0) bonded to the generator set chassis.  The grounding bus of the three-pole automatic transfer switch (ATS) shall be bonded to the existing equipment grounding system to be identified by contractor in the field.  Neutral and ground shall not be connected at the generator.  The contractor shall ensure that at the completion of this work, that there is one and only one neutral-ground bond for the incoming service.

  - Generator Fuel Supply: Contractor shall provide and install the necessary fuel supply and return lines in accordance with the requirement of the engine manufacturer.  All fuel lines shall be black iron pipe suitable for diesel fuel and sized for the engine capacity or as recommended by the engine manufacturer.  The generator shall have a 2,000L or larger double-walled fuel tank within the generator enclosure.  The contractor shall provide all fuel needed for testing and shall fill the tank after all testing and prior to departure from the job site.

  - Equipment Concrete Foundation and Slab On Grade: Provide generator set concrete and steel reinforced foundation in accordance with the recommendation of the generator set manufacturer.  Provide steel reinforced concrete foundation and slab on grade to accommodate the total weight of the equipment and weatherproof enclosure.  The generator and slab shall be placed to allow a minimum 3 foot walk space between the generator and the Consular Building exterior wall, and to allow manufacturer recommended clearances on all sides of the generator.

  - Generator Exterior Lighting:  Weatherproof fluorescent lighting fixtures using T8 fluorescent bulbs and electronic ballasts shall be added to the Consular exterior wall to provide a minimum of 5 footcandles of illumination in the immediate generator vicinity.

  - Generator Air Flow:  Ventilation and exhaust shall be oriented and placed by the contractor to provide recommended air flow volume and flow patterns to properly cool the generator in all running scenarios, and to avoid damage to surrounding structures and vegetation.

  - Load Balancing: The loads on the generator and Main Distribution Panel (Panel MDP) shall be balanced by the contractor.

  - Lansdscaping and Paving:  The contractor shall be responsible for any trenching, refill, paving, or painting needed to restore the site to similar condition after the work is finished.

5.0	OTHER MISCELLANEOUS REQUIREMENTS

  - Electric Power Availability: The Consulate is an operational facility, therefore, the contractor shall ensure that electric power is available at all times except on scheduled outages acceptable to the contracting officer’s representative (COR).  During the implementation of this SOW, the contractor shall diligently schedule the work to minimize downtime, and if a power outage is required, the contractor shall submit the request for a power outage no less than two calendar days in advance.  The US Government can deny or defer a requested outage if they see the need.  All outages shall be scheduled outside of normal operational hours.

  - Contractor’s Inspection of Work: Contractor shall diligently inspect the work to ensure that the equipment is installed in accordance with the manufacturer’s instructions, and all wiring and conduit systems are installed in accordance with the U.S. National Electrical Code, and the local electrical code.

  - Operation Sequence: The new generator and ATS shall be set up to provide generator power automatically when utility power is lost or is outside of acceptable parameters, and to return to utility power after utility power is restored to acceptable parameters.  The load shall be automatically placed on generator power when any one phase is outside the parameters provided in the SOW Attachment 1.

  - Contractor Contact:  A responsible contractor contact shall be designated for the duration of the project.  That contractor shall provide the Embassy contact with a local mobile phone number.

6.0	TESTING & COORDINATION

6.1	Preliminary Testing:  Contractor shall coordinate and advise the COR of schedule of final testing to arrange for Government witnesses.  All preliminary testing of the generator set including the automatic transfer switch shall be accomplished in accordance with the manufacturer’s testing requirements, and shall be conducted when loss of power during the transfers will have minimum effect on critical building loads.  The contractor shall report, in writing, the result of the testing for:

- Engine-generator Safety and Alarms: The Contractor shall perform testing to verify that all engine-generator alarms and shutdown devices work as designed.

- Engine generator load testing: The Contractor shall perform all testing required to verify the proper operation of the complete generator power system (in a simulated loss of utility power) for a minimum of four hours run time on generator.

  - Testing Witnessing: The above test shall be repeated twice consecutively without any abnormalities as a minimum to ensure the systems will function satisfactorily as designed. The Government shall witness this testing and provide acceptance of the results.  The Contractor shall submit the detailed written result of the operational testing, and shall certify the overall result, pass or fail.  With Contracting Officer’s Technical Representative (COR) approval, the contractor shall correct any problem discovered during the above tests.  Re-testing of the system shall be coordinated with the COR until a passing (satisfactory) result is obtained.

  - Demolition and Removal:  All removed materials and equipment shall be removed and disposed of by the contractor in a proper manner.

  - Training:  The contractor shall provide not less than four hours training to all interested Embassy personnel in operation, maintenance, and troubleshooting of the new generator set and automatic transfer switch.

- EMBASSY INSPECTION AND ACCEPTANCE

Upon successful testing and demonstration of the completed project, the contractor shall submit written operation testing results, and copies of completed manufacturer’s recommended testing checklists.  Embassy Contracting Officer or his representative shall then conduct the final inspection and acceptance of the project and prepare the project acceptance documentation.

- WARRANTY

All contractor supplied equipment and all work performed by the contractor shall have a one-year warranty from date of Government’s acceptance of the overall project, not from the date that the generator is first operated.  Contractor shall furnish the name, address and telephone number of guarantor or his representative to notify in the event of a failure in the standby power system during the warranty period. Contractor shall also provide a written list of manufacturer’s warranties associated with the material/equipment installed; furnish the name, address and telephone number of the guarantor’s representative of the equipment being furnished.  Contractor or his representative shall coordinate with the material/equipment manufacturer, upon request by the Embassy or his representative, shall honor the warranty during the warranty period, and shall provide the services under this warranty as necessary to repair the equipment specified in this contract.  Labor and material incurred during the repair or replacement of parts/equipment under the warranty period shall be at contractor’s expense and at no cost to the U.S. Government.  It must be stressed that the warranty is the full responsibility of the contractor, and the contractor must respond to provide warranty repairs within 24 hours of reported problems.  If the contractor chooses, he may pursue reimbursement under an equipment manufacturer warranty, but that shall not be a reason to delay or defer his warranty service.

  - CONTRACTOR SERVICES

The contractor shall provide all installation drawings, materials, labor, project inspection, coordination and testing and other incidental work for a complete operational generator power system.  The installation drawings shall be prepared by the contractor, and submitted to the Contracting Officer Representative (COR) for review and approval.  Contractor shall carry out the work in accordance with the COR approved installation drawings.  No work may start without approved installation drawings.

- DRAWING FORMAT

All installation drawings shall be in hard metric.  All drawings, specifications, if any and correspondence shall be in English.  All drawings shall be the same size, approximately 0.60m x 0.90m.   All drawings shall be in AutoCAD file Data Disks and in PDF.  Upon completion of the project, the Contractor shall submit two sets of as-built installation drawings to the Contracting Officer for Embassy and OBO/OM/FAC distribution.  In addition, the contractor must provide two sets of AutoCAD and PDF drawing files in diskette (one for Embassy and one for OBO/OM/FAC).

- PRICE AND STEPS

11.1     Provide a fixed cost price in US dollars to meet this scope of work.  The fixed cost price shall include all direct costs for labor, materials, and equipment, and burdens for overhead profit and taxes. The Contractor shall submit the cost proposal for each task towards installation of a completely operational generator power system in accordance with the requirements specified in this Scope of Work.  Costs proposed for each task shall be subject to negotiation.

    - Site Survey:  Perform a site survey and determine site conditions, existing equipment layout, and location of electrical services and panels. Determine location and orientation of the new generator set with emphasis on proper exhaust, ventilation, and air flow to allow proper operation per manufacturer requirements.

    - Preparation of Installation Drawings: Prepare installation drawings, specifications, and Bill of Materials in accordance with this scope of work and generator set specification and from the information found during the site survey.  Installation drawings shall also incorporate the requirements of the equipment manufacturer’s installation instructions.  All field wiring shall be in accordance with the U.S. National Electrical Code, and the local electrical Code, and installation requirements of the generator and ATS manufacturers.

    - Installation:  Upon COR notification of installation drawings approval and notice to proceed on installation, the contractor shall commence procurement of materials and mobilization to implement the project.  Provide all materials, equipment, trenching and backfill, and labor for a complete operational generator power system, including all accessories, incidentals, and miscellaneous work such as the modification of the power distribution system to phase-in the generator set, required testing in accordance with the requirement of this scope of work, and any civil works needed to accomplish the project successfully.

- ADMINISTRATIVE REQUIREMENTS

Meetings: The Contractor shall attend a minimum of three meetings with the Embassy representatives.  For planning purposes, these meetings shall be site survey, installation progress review, and project acceptance testing meeting.  Schedule dates for the meeting shall be determined by the COR and all concerned.

- INSTALLATION REQUIREMENTS

  - General: All materials to be installed shall be all new.  The Contractor shall carry out the installation in accordance with the contractor prepared, COR approved installation drawings.  The contractor shall manage, administer, supervise and inspect the installation.  The proper management of all work shall be the sole responsibility of the contractor.  Coordination shall be continuous during the installation phase with the on-site US Government representative.

  - Safety: Safety is the highest priority on this and all US Embassy projects.  The contractor shall direct all of those under his charge to work safely.  Regular safety meetings shall be held among on-site contractor personnel, and safety concerns shall be brought to the attention of the Post Safety and Health Officer (POSHO) and the COR.

  - Installation Submission Requirements:  Prior to commencement of installation, the contractor shall provide the Contracting Officer the following for his/her review and approval to ensure conformance with the contract requirements:

- Detailed contractor Organization description including list of subcontractors, if any and description of roles.  Personal information on all individuals involved in the project shall be submitted to the Embassy Regional Security Office (RSO) for site clearances.

- Detailed installation schedule describing each key installation activity.  The contractor shall develop all activities to minimize power interruptions affecting Consular Building operations.

  - Contractor Personnel: The contractor shall furnish sufficient personnel with the technical knowledge and experience necessary to complete the work. The contractor shall designate an English speaking contractor’s site supervisor who will be responsible for all contractor personnel and daily work as needed.  The contractor shall inspect the job site for progress and ensure work is accomplished in accordance with this scope of work.

  - Documentation: The contractor shall obtain, maintain, and pay for all required insurance, licenses, permits and certificates, if required to perform the work prior to commencement and for the duration of the work.

  - Schedule: The contractor shall carefully execute the work in a manner acceptable to the Contracting Officer, and avoid interference or accidental damage to the government equipment or existing property.  All scheduling shall be coordinated with the Contracting Officer or his/her representative. Onsite electrical installation work at the Consular Building is required to be completed in less than 20 calendar days on site from start to finish. Onsite civil work may be done in advance of the electrical work.  If the contractor is unable to comply with these dates, he must state this clearly in his cost submittal and must denote an alternate schedule that he can meet.

  - Work Organization and Restoration: The contractor must recognize that this is an important representational property for the US Government and shall keep the work site clean and organized.  The contractor shall clean up the site daily before departure from the site and shall dispose of all debris from the work areas. The contractor shall backfill all trenching, and shall provide safety barriers around all open trenching.

  - Final Interconnection: The contractor shall coordinate with the COR to make final cable/wiring connections to the existing power distribution system including its modification.

  - Site Access: Contractor will have the use of the project site in its entirety within security guidelines, coordinating access with Embassy representatives.  The contractor will receive the right of entry and compound access to the project site after the Notice to Proceed of installation.  Once the site work begins, the contractor shall be responsible for compliance with the Embassy security rules and regulations.

  - Coordination: Contractor shall coordinate with the Embassy representatives and secure approval for site area authorization within the contract limits such as for mobilization, operation of contractor’s equipment, and storage.  At substantial completion of the project, all mobilization support equipment and accessories shall be removed from the site.  Before the project is closed out, and in accordance with the approved installation schedule, the site shall be cleared of all installation debris and other materials, and restored to original pre-installation condition.  All contractor vehicles must remain outside of the Consulate property except for prearranged delivery and removal of materials.  The will be no parking within the property.

  - Construction Power: During installation, the contractor shall provide temporary power from Consulate power sources for his use as needed.  The contractor shall ensure that he does not overload any circuits that he uses for temporary power. The contractor shall not be charged for temporary power taken after the Consulate meter. This requirement shall be coordinated with the Embassy representatives in advance to determine the power source connections.  The contractor shall remove the temporary power connections after completion of the project.  All temporary connections shall be properly protected electrically and safe for area personnel.

  - Existing Facilities/Buildings: The contractor shall exercise care not to damage existing facilities and equipment during installation.  Existing facilities and existing equipment which are damaged, accidental or not, shall be repaired or restored to original condition at no cost to the U.S. Government.  Building alterations shall be coordinated in advance with Embassy representatives.  Opening or removing perimeter walls or doors must be coordinated in advance with Embassy security personnel.

- PREPARATION OF INSTALLATION DRAWINGS: SUBMISSION

REQUIREMENTS

  - Submittal:  Prior to equipment procurement and installation, the contractor shall submit to COR, two (2) sets of installation drawings, specifications of materials/equipment to be procured, including catalog data/cut sheets of equipment and materials, and his installation schedules for COR review and approval.  The specifications or catalog data/cut sheets of equipment must include the generator, ATS, circuit breakers, batteries, battery charger, conduit, electrical cables, etc.

  - Government Review: The US Government shall review the contractor furnished submittal documents above for conformance with the contract requirements within 21 calendar days of receipt. Review comments will be provided to the contractor, in writing.

  - Incorporation of Changes: Contractor shall respond to the comments in writing within 21 calendar days of receipt and incorporate comments into the final installation drawings.  Comments not accepted by the contractor shall be brought to the COR in writing immediately for resolution.  Decisions by the COR with respect to incorporation of comments deemed to be within the scope of work of this project will be final.  Review comments recognized by the COR requiring actions outside this scope of work requires contract modification and will not be required until the CO issues a Notice to Proceed.  Any comments if within the scope of work, as judged by the CO, shall be incorporated into the final installation drawings at no additional cost to the Government.

  - Work Quality: Any work rejected by the CO as incomplete, erroneous, uncoordinated, or not meeting the scope of work requirements, shall be corrected and resubmitted within 21 calendar days of notification.

  - Drawing Maintenance: The contractor shall furnish final as-built installation drawings to the U.S. Government at the conclusion of the project.

- PROJECT SCHEDULE

The installation work is desired to commence no later than June 30, 2008.  An alternate commencement date shall be coordinated with the CO as needed by the US Government.  The on-site electrical installation work shall be completed within 20 calendar days of start.  The civil work may be done in advance of the electrical at any time after the approval of the installation drawings.  The contractor shall not deliver any equipment or materials to the site prior to the agreed start date.

- DELIVERABLE DOCUMENTS

- Two (2) sets of Installation Drawings (100% complete) for Government review sent by Federal Express or other three day or less delivery method. One set shall be sent to the CO and one set to the Electrical Engineer in Springfield, VA at the address provided in this SOW.

- Two (2) sets of Installation Drawings (FINAL document) sent by Federal Express or other three day or less delivery method for Government review after all review comments are incorporated and installation drawings issues are resolved.  One set shall be sent to the CO and one set to the Electrical Engineer in Springfield, VA.  This step can be skipped if there are no changes to the drawings submitted in Part (a) above.  This step shall be repeated until acceptable and correct drawings are accepted.

- After completion of the installation, two (2) sets of as-built drawings shall be provided for Government record. One set shall be sent to the CO and one set to the Electrical Engineer in Springfield, VA.

- After completion of the installation, two sets of AutoCAD file data disk containing the as-built drawings shall be provided.  One of the sets shall be forwarded to the CO and one set to the Electrical Engineer in Springfield, VA.

- Minimum two sets of maintenance, operation, and troubleshooting manuals and manufacturers warranties clearly showing serial numbers for the generator set and automatic transfer switch shall be provided. One of the sets shall be forwarded to the CO and one set to the Electrical Engineer in Springfield, VA.

(g)    Submission shall be forwarded to the following by DHL:

- Contracting Officer

Maura Pellet,  U.S. American Embassy Kyiv

Kyiv, Ukraine

- Mr. Richard Crowson, PE

Tel: 703-452-8883

## Electrical Engineer

## Fax: 703-452-8841

## US Department Of State

OBO/OM/FAC/PS

8380 Alban Rd

Springfield, Virginia  22150

E-mail: CrowsonRH@state.gov

16.0     CONTRACTING OFFICER’S REPRESENTATIVE (COR)

The COR for this project is:

Alan Sprague, Facility Manager                  	Tel: 3-8-044-490-4020

U.S. Embassy Kyiv                                                 Fax:  3-8-044-490-4085

Kyiv, Ukraine

Email:  SpragueAF@State.gov

ATTACHMENTS to the Scope of Work:

- STANDBY GENERATOR/AUTOMATIC TRANSFER SWITCH TECHNICAL REQUIREMENTS

- EXISTING ELECTRICAL ONE-LINE

- PROPOSED ELECTRICAL ONE-LINE

ATTACHMENT 1

STANDBY GENERATOR/AUTOMATIC TRANSFER

SWITCH TECHNICAL REQUIREMENTS

U.S. Consulate Building – Kyiv, Ukraine

- INTRODUCTION

This Attachment contains technical requirements related to the diesel generator and Automatic Transfer Switch (ATS).

- OPERATING ENVIRONMENT

All system components are required to start, provide continuous full rated load, and perform within specifications for the following environmental conditions:

  - Ambient temperature:	-40o C to 40o C

  - Relative humidity:	up to 100%

  - Elevation:	up to 500 meters

- EQUIPMENT TO FURNISH AND INSTALL

  - One (1) Diesel-Generator Set in outdoor-rated enclosure

To be rated 1500 RPM, 50 Hz, 100 kVA (80kW) or higher, 380Y/220 Volts, 3-phase, 4-wire, for standby duty.

The diesel-generator set is to include one (1) skid mounted radiator cooled diesel-generator complete with all standard features and the following:

    - Generator to be single bearing, static regulated, brushless, air cooled, self-ventilated.

    - Vibration isolated control panel to include:

- Automatic/manual start stop controls

- Ammeter and voltmeter with phase selector switch

- Frequency meter

- Run-hour meter

- Safety shutdowns to include overspeed, low oil pressure, high water temperature, overcrank, low coolant level, and emergency stop push button.

- Voltage and frequency adjustment provisions

    - Volts per Hertz compensated solid state voltage regulator. Steady state voltage regulation to be ( 0.5% of rated voltage for all loads from no load to 100% load.

    - Electronic governor to control engine speed. Steady state frequency regulation to be ( 0.5% of rated frequency for constant loads from no load to 100% load.

    - Thermostatically controlled jacket water heater to maintain 32o C water temperature. Water heater to be for 220 or 380 V, 50 Hz power supply. Heater power supply to terminate at customer connection terminal board.

    - Anti-condensation heater for generator. Heater to be for 220 or 380 V, 50 Hz power supply. Heater power supply to terminate at customer connection terminal board.

    - One (1) heavy-duty 24 VDC lead-acid battery, battery rack, and battery cables. Battery capacity to be sufficient to provide three (3) fifteen-second engine cranking cycles for all operating environments defined in Section 2. Battery capacity is based upon maximum time of one (1) minute between cranking cycles, and no battery recharge allowed between cranking cycles.

    - One (1) generator mounted 3-pole UL or CE listed main circuit breaker. Circuit breaker to have isolated neutral, and be rated for 380 V 50/60 Hz application.

    - One (1) 10-ampere automatic float/equalizing battery charger suitable for the batteries specified in Paragraph 3.1.7. Battery charger to be for a 220 V, 50 Hz power supply.

    - Critical-grade exhaust silencer. Sound level not to exceed 78 dBA at 7 meters from the generator enclosure.

    - Transient performance of diesel engine-generator to be as follows for application or removal of load steps of up to 50% rated load:

      - Maximum voltage variation not more than 10%

      - Maximum frequency variation not more than 5%.

Both voltage and frequency are to recover to the steady state operation band within five (5) seconds.

    - Engine lubricating oil

    - Antifreeze (coolant)

    - Fuel line water separator

    - Vibration Isolators

    - Spare parts sufficient for scheduled maintenance specified in the service manual for one year (1000 operating hours). Spare parts to also include two (2) sets of all fuses, indicating lamps, and spare keys.

    - Two (2) sets of installation, operation, and maintenance manuals. Include a complete parts list for the unit, and schematic diagrams.

    - One-year warranty covering defects in materials and workmanship, beginning on the date the installation project is accepted by the US Government.

    - Prior to delivery to site, perform standard factory tests on the diesel-generator. Factory tests to include a continuous load bank test (resistive acceptable) prior to shipment. Load bank test to include 50% block load application and removal, 75% block load application and removal, 1 hour at 50% rated load, and 1 hour at 100% rated load. Test report including continuous log record of frequency, phase voltages, and phase currents.

Diesel-generator must perform within specifications (Paragraphs 3.1.3, 3.1.4, 3.1.10 & 3.1.12) for the entire duration of this test.

  - One (1) Automatic Transfer Switch

The Automatic Transfer Switch (ATS) to be UL 1008 listed, 200 ampere rated or higher per manufacturer sizing recommendations, 380/220 Volt, 50 Hertz, 3-pole with solid isolated neutral. Short circuit withstand rating not less than 30,000 amperes rms symmetrical, complete with all standard features and the following:

    - NEMA Type 3 (outdoor) rated

    - Automatic and manual operation mechanically and electrically interlocked to prevent simultaneous connection of any two sources.

    - Double throw automatic operation including starting and stopping of generator, transfer and retransfer of load, with field adjustable pickup and dropout settings, and generator start when utility source voltage is below 80% or above 115% of nominal, or frequency is below 98% or above 102% of nominal.

Automatic retransfer to utility source, and engine-generator shutdown with manufacturer recommended cool-down, when utility source voltage and frequency are restored to normal.

    - Three phase over/under voltage sensing.

    - One phase over/under frequency sensing.

    - Time delay on engine start field adjustable up to 10 seconds. Set at 5 seconds.

    - Time delay on re-transfer to utility source field adjustable up to 30 minutes. Set at 10 minutes.

    - Engine cool down timer adjustable 1-30 minutes. Set at 10 minutes.

    - Test switch to simulate normal power failure.

    - For the transfer switch, two (2) extra sets of all fuses and all lamps.

    - Lugs for normal, load, generator, and neutral cables to be mechanical not compression type.

    - Two (2) sets of installation, operation, and maintenance manuals for the transfer switch. Include a complete parts list for the ATS, and schematic diagrams.

    - One-year warranty covering defects in materials and workmanship, beginning on the date the installation project is accepted by the U.S. Government.

C.	PACKAGING AND MARKING

Mark materials delivered to the site as follows:

US Embassy, Kyiv

Pimonenko St.

Consular Building

1

D. INSPECTION AND ACCEPTANCE

The COR, or his/her authorized representatives, will inspect from time to time the services being performed and the supplies furnished to determine whether work is being performed in a satisfactory manner, and that all supplies are of acceptable quality and standards.

The Contractor shall be responsible for any countermeasures or corrective action, within the scope of this contract, which may be required by the Contracting Officer as a result of such inspection.

Substantial Completion:  Definitions

(a) "Substantial Completion" means the stage in the progress of the work as determined and certified by the Contracting Officer in writing to the Contractor, on which the work (or a portion designated by the Government) is sufficiently complete and satisfactory.  Substantial completion means that the property may be occupied or used for the purpose for which it is intended, and only minor items such as touch-up, adjustments, and minor replacements or installations remain to be completed or corrected which:

(1) do not interfere with the intended occupancy or utilization of the work, and

(2) can be completed or corrected within the time period required for final completion.

(b) The "date of substantial completion" means the date determined by the Contracting Officer or authorized Government representative as of which substantial completion of the work has been achieved.

Use and Possession upon Substantial Completion

The Government shall have the right to take possession of and use the work upon substantial completion.  Upon notice by the Contractor that the work is substantially complete (a Request for Substantial Completion) and an inspection by the Contracting Officer or an authorized Government representative (including any required tests), the Contracting Officer shall furnish the Contractor a Certificate of Substantial Completion.  The certificate will be accompanied by a Schedule of Defects listing items of work remaining to be performed, completed or corrected before final completion and acceptance.  Failure of the Contracting Officer to list any item of work shall not relieve the Contractor of responsibility for complying with the terms of the contract.  The Government's possession or use upon substantial completion shall not be deemed an acceptance of any work under the contract.

Final Completion and Acceptance:  Definitions

(a) "Final completion and acceptance" means the stage in the progress of the work as determined by the Contracting Officer and confirmed in writing to the Contractor, at which all work required under the contract has been completed in a satisfactory manner, subject to the discovery of defects after final completion, and except for items specifically excluded in the notice of final acceptance.

(b) The "date of final completion and acceptance" means the date determined by the Contracting Officer when final completion of the work has been achieved, as indicated by written notice to the Contractor.

Final Inspection and Tests

The Contractor shall give the Contracting Officer at least five (5) days advance written notice of the date when the work will be fully completed and ready for final inspection and tests.  Final inspection and tests will be started not later than the date specified in the notice unless the Contracting Officer determines that the work is not ready for final inspection and so informs the Contractor.

Final Acceptance

If the Contracting Officer is satisfied that the work under the contract is complete (with the exception of continuing obligations), the Contracting Officer shall issue to the Contractor a notice of final acceptance and make final payment upon:

-Satisfactory completion of all required tests,

-a final inspection that all items by the Contracting Officer listed in the Schedule of Defects have been completed or corrected and that the work is finally complete (subject to the discovery of defects after final completion), and

-submittal by the Contractor of all documents and other items required upon completion of the work, including a final request for payment (Request for Final Acceptance).

E - DELIVERIES OR PERFORMANCE

52.211-10  COMMENCEMENT, PROSECUTION, AND COMPLETION OF WORK

(APR 1984)

The Contractor shall be required to:

- (a)    commence work under this contract within   10 calendar days after the date the Contractor receives the notice to proceed,

- (b)   prosecute the work diligently, and,

- (c)    complete the entire work ready for use not later than 90 days after NTP.

The time stated for completion shall include final cleanup of the premises and completion of punch list items.

52.211-12 LIQUIDATED DAMAGES - CONSTRUCTION (SEP 2000)

(a)	If the Contractor fails to complete the work within the time specified in the contract, or any extension, the Contractor shall pay liquidated damages to the Government in the amount of 140.00 USD for each calendar day of delay until the work is completed or accepted.

(b)	If the Government terminates the Contractor’s right to proceed, liquidated damages will continue to accrue until the work is completed.  These liquidated damages are in addition to excess costs of repurchase under the Default clause.

CONTRACTOR'S SUBMISSION OF CONSTRUCTION SCHEDULES

(a)	The time for submission of the schedules referenced in FAR 52.236-15, "Schedules for Construction Contracts", paragraph (a), is hereby modified to reflect the due date for submission as “5 calendar days after receipt of an executed contract”.

(b)	These schedules shall include the time by which shop drawings, product data, samples and other submittals required by the contract will be submitted for approval.

(c)	The Contractor shall revise such schedules (1) to account for the actual progress of the work, (2) to reflect approved adjustments in the performance schedule, and (3) as required by the Contracting Officer to achieve coordination with work by the Government and any separate contractors used by the Government.  The Contractor shall submit a schedule, which sequences work so as to minimize disruption at the job site.

(d)	All deliverables shall be in the English language and any system of dimensions (English or metric) shown shall be consistent with that used in the contract.  No extension of time shall be allowed due to delay by the Government in approving such deliverables if the Contractor has failed to act promptly and responsively in submitting its deliverables.  The contractor shall identify each deliverable as required by the contract.

(e)	Acceptance of Schedule:  When the Government has accepted any time schedule; it shall be binding upon the Contractor.  The completion date is fixed and may be extended only by a written contract modification signed by the Contracting Officer.  Acceptance or approval of any schedule or revision thereof by the Government shall not:

- (1)   Extend the completion date or obligate the Government to do so,

- (2)   Constitute acceptance or approval of any delay, or

- (3)   Excuse the Contractor from or relieve the Contractor of its obligation to maintain the progress of the work and achieve final completion by the established completion date.

Notice Of Delay

If the Contractor receives a notice of any change in the work, or if any other conditions arise which are likely to cause or are actually causing delays which the Contractor believes may result in late completion of the project, the Contractor shall notify the Contracting Officer.  The Contractor’s notice shall state the effect, if any, of such change or other conditions upon the approved schedule, and shall state in what respects, if any, the relevant schedule or the completion date should be revised.  The Contractor shall give such notice promptly, not more than ten (10) days after the first event giving rise to the delay or prospective delay. Only the Contracting Officer may make revisions to the approved time schedule.

Notice to Proceed

(a)	After receiving and accepting any bonds or evidence of insurance, the Contracting Officer will provide the Contractor a Notice to Proceed.  The Contractor must then prosecute the work, commencing and completing performance not later than the time period established in the contract.

(b)	It is possible that the Contracting Officer may elect to issue the Notice to Proceed before receipt and acceptance of any bonds or evidence of insurance.  Issuance of a Notice to Proceed by the Government before receipt of the required bonds or insurance certificates or policies shall not be a waiver of the requirement to furnish these documents.

Working Hours

All work shall be performed during 9:00-18:00 in regular working days.  Other hours, if requested by the Contractor, may be approved by the Contracting Officer's Representative (COR).  The Contractor shall give 24 hours in advance to COR who will consider any deviation from the hours identified above.  Changes in work hours, initiated by the Contractor, will not be a cause for a price increase.

Preconstruction Conference

A preconstruction conference will be held 10 days after contract award at Glubochytska 4, Artem Business Center to discuss the schedule, submittals, notice to proceed, mobilization and other important issues that effect construction progress.  See FAR 52.236-26, Preconstruction Conference.

Deliverables

The following items shall be delivered under this contract:

Description				Quantity	Delivery Date		Deliver to:

G.  Securities/Insurance		1		10 days after award	Contracting Officer

E. Construction Schedule		1		10 days after award	COR

E   Preconstruction Conference	1		10 days after award 	COR

G.  Personnel Biographies		1		10 days after award	COR

F.  Payment Request		1		last calendar day of	COR

each month

D.  Request for Substantial Completion 1		15 days before inspection COR

D Request for Final Acceptance	1		5 days before inspection COR

F  ADMINISTRATIVE DATA

652.242-70 CONTRACTING OFFICER'S REPRESENTATIVE (COR) (AUG 1999)

(a)	The Contracting Officer may designate in writing one or more Government employees, by name or position title, to take action for the Contracting Officer under this contract. Each designee shall be identified as a Contracting Officer’s Representative (COR). Such designation(s) shall specify the scope and limitations of the authority so delegated; provided, that the designee shall not change the terms or conditions of the contract, unless the COR is a warranted Contracting Officer and this authority is delegated in the designation.

(b)	The COR for this contract is Alan Sprague, Facility Maintenance Manager.

Payment: The Contractor's attention is directed to Section H, 52.232-5, "Payments Under Fixed-Price Construction Contracts".  The following elaborates on the information contained in that clause.

Requests for payment, may be made no more frequently than monthly.  Payment requests shall cover the value of labor and materials completed and in place, including a prorated portion of overhead and profit.

After receipt of the Contractor's request for payment, and on the basis of an inspection of the work, the Contracting Officer shall make a determination as to the amount, which is then due.  If the Contracting Officer does not approve payment of the full amount applied for, less the retainage allowed by in 52.232-5, the Contracting Officer shall advise the Contractor as to the reasons.

Under the authority of 52.232-27(a), the 14 day period identified in FAR 52.232-27(a)(1)(i)(A) is hereby changed to 30 days.

The contractor shall show Value Added Tax (VAT) as a separate item on invoices submitted for payment.

G. SPECIAL REQUIREMENTS

Performance/Payment Protection

The Contractor shall furnish some form of payment protection as described in 52.228-13  in the amount of  10% of the contract price.

The Contractor shall provide the information required by the paragraph above within ten (10) calendar days after award.  Failure to timely submit the required security may result in rescinding or termination of the contract by the Government.  If the contract is terminated, the contractor will be liable for those costs as described in FAR 52.249-10, Default (Fixed-Price Construction), which is included in this purchase order.

The bonds or alternate performance security shall guarantee the Contractor's execution and completion of the work within the contract time.  This security shall also guarantee the correction of any defects after completion, the payment of all wages and other amounts payable by the Contractor under its subcontracts or for labor and materials, and the satisfaction or removal of any liens or encumbrances placed on the work.

The required securities shall remain in effect in the full amount required until final acceptance of the project by the Government.  Upon final acceptance, the penal sum of the performance security shall be reduced to 10% of the contract price.  The security shall remain in effect for one year after the date of final completion and acceptance, and the Contractor shall pay any premium required for the entire period of coverage.

Insurance

The Contractor is required by FAR 52.228-5, "Insurance - Work on a Government Installation" to provide whatever insurance is legally necessary.  The Contractor shall at its own expense provide and maintain during the entire performance period the following insurance amounts:

General Liability (includes premises/operations, collapse hazard, products, completed operations, contractual, independent contractors, broad form property damage, personal injury)

1.  Bodily Injury on or off the site stated in US Dollars:

Per Occurrence                 $2,000.00

Cumulative                       $10,000.00

- Property Damage on or off the site in US Dollars:

Per Occurrence               $5,000.00

Cumulative                     $35,000.00

The foregoing types and amounts of insurance are the minimums required.  The Contractor shall obtain any other types of insurance required by local law or that are ordinarily or customarily obtained in the location of the work.  The limit of such insurance shall be as provided by law or sufficient to meet normal and customary claims.

The Contractor agrees that the Government shall not be responsible for personal injuries or for damages to any property of the Contractor, its officers, agents, servants, and employees, or any other person, arising from and incident to the Contractor's performance of this contract.  The Contractor shall hold harmless and indemnify the Government from any and all claims arising therefrom, except in the instance of gross negligence on the part of the Government.

The Contractor shall obtain adequate insurance for damage to, or theft of, materials and equipment in insurance coverage for loose transit to the site or in storage on or off the site.

The general liability policy required of the Contractor shall name "the United States of America, acting by and through the Department of State", as an additional insured with respect to operations performed under this contract.

Document Descriptions

Supplemental Documents:  The Contracting Officer shall furnish from time to time such detailed drawings and other information as is considered necessary, in the opinion of the Contracting Officer, to interpret, clarify, supplement, or correct inconsistencies, errors or omissions in the Contract documents, or to describe minor changes in the work not involving an increase in the contract price or extension of the contract time.  The Contractor shall comply with the requirements of the supplemental documents, and unless prompt objection is made by the Contractor within 20 days, their issuance shall not provide for any claim for an increase in the Contract price or an extension of contract time.

Record Documents.  The Contractor shall maintain at the project site:

- (1)  a current marked set of Contract drawings and specifications indicating all interpretations and clarification, contract modifications, change orders, or any other departure from the contract requirements approved by the Contracting Officer; and,

- (2)  a complete set of record shop drawings, product data, samples and other submittals as approved by the Contracting Officer.

"As-Built" Documents:  After final completion of the work, but before final acceptance thereof, the Contractor shall provide:

- (1)  a complete set of "as-built" drawings, based upon the record set of drawings, marked to show the details of construction as actually accomplished; and,

- (2)  record shop drawings and other submittals, in the number and form as required by the specifications.

Laws and Regulations

The Contractor shall, without additional expense to the Government, be responsible for complying with all laws, codes, ordinances, and regulations applicable to the performance of the work, including those of the host country, and with the lawful orders of any governmental authority having jurisdiction.  Host country authorities may not enter the construction site without the permission of the Contracting Officer.  Unless otherwise directed by the Contracting Officer, the Contractor shall comply with the more stringent of the requirements of such laws, regulations and orders and of the contract.  In the event of a conflict between the contract and such laws, regulations and orders, the Contractor shall promptly advise the Contracting Officer of the conflict and of the Contractor's proposed course of action for resolution by the Contracting Officer.

The Contractor shall comply with all local labor laws, regulations, customs and practices pertaining to labor, safety, and similar matters, to the extent that such compliance is not inconsistent with the requirements of this contract.

The Contractor shall give written assurance to the Contracting Officer that all subcontractors and others performing work on or for the project have obtained all requisite licenses and permits.

The Contractor shall submit proper documentation and evidence satisfactory to the Contracting Officer of compliance with this clause.

Construction Personnel

The Contractor shall maintain discipline at the site and at all times take all reasonable precautions to prevent any unlawful, riotous, or disorderly conduct by or among those employed at the site.  The contractor shall ensure the preservation of peace and protection of persons and property in the neighborhood of the project against such action.  The Contracting Officer may require, in writing, that the Contractor remove from the work any employee that the Contracting Officer deems incompetent, careless, insubordinate or otherwise objectionable, or whose continued employment on the project is deemed by the Contracting Officer to be contrary to the Government's interests.

If the Contractor has knowledge that any actual or potential labor dispute is delaying or threatens to delay the timely performance of this contract, the Contractor shall immediately give notice, including all relevant information, to the Contracting Officer.

After award, the Contractor has ten calendar days to submit to the Contracting Officer a list of workers and supervisors assigned to this project for the Government to conduct all necessary security checks.  It is anticipated that security checks will take 10 days to perform.  For each individual the list shall include:

Full Name

Place and Date of Birth

Current Address

Copy of Passport

Failure to provide any of the above information may be considered grounds for rejection and/or resubmittal of the application.  Once the Government has completed the security screening and approved the applicants a badge will be provided to the individual for access to the site. This badge may be revoked at any time due to the falsification of data, or misconduct on site.

The Contractor shall provide an English-speaking supervisor on site at all times.  This position is considered as key personnel under this purchase order.

Materials and Equipment

All materials and equipment incorporated into the work shall be new and for the purpose intended, unless otherwise specified.  All workmanship shall be of good quality and performed in a skillful manner that will withstand inspection by the Contracting Officer.

Special Warranties

Any special warranties that may be required under the contract shall be subject to the stipulations set forth in 52.246-21, "Warranty of Construction", as long as they are not in conflict.

The Contractor shall obtain and furnish to the Government all information required to make any subcontractor's, manufacturer's, or supplier's guarantee or warranty legally binding and effective.  The contractor shall submit both the information and the guarantee or warranty to the Government in sufficient time to permit the Government to meet any time limit specified in the guarantee or warranty, but not later than completion and acceptance of all work under this contract.

Equitable Adjustments

Any circumstance for which the contract provides an equitable adjustment that causes a change within the meaning of paragraph (a) of the "Changes" clause shall be treated as a change under that clause; provided, that the Contractor gives the Contracting Officer prompt written notice (within 20 days) stating:

- (a)    the date, circumstances, and applicable contract clause authorizing an equitable adjustment and

- (b)   that the Contractor regards the event as a changed condition for which an equitable adjustment is allowed under the contract.

The Contractor shall provide written notice of a differing site condition within 10 calendar days of occurrence following FAR 52.236-2, Differing Site Conditions.

Zoning Approvals and Permits

The Government shall be responsible for:

-       obtaining proper zoning or other land use control approval for the project

-       obtaining the approval of the Contracting Drawings and Specifications

-       paying fees due for the foregoing; and,

-       for obtaining and paying for the initial building permits.

H. CLAUSES

52.252-2 CLAUSES INCORPORATED BY REFERENCE (FEB 1998)

This contract incorporates one or more clauses by reference, with the same force and effect as if they were given in full text. Upon request, the Contracting Officer will make their full text available. Also, the full text of a clause may be accessed electronically at this/these address(es):

http://www.arnet.gov/far   or,   http://farsite.hill.af.mil/search.htm

These addresses are subject to change.  If the Federal Acquisition Regulation (FAR) is not available at the locations indicated above, use the Dept. of State Acquisition Website at http://www.statebuy.gov/home.htm to see the links to the FAR.   You may also use an Internet “search engine” (e.g., Yahoo, Excite, Alta Vista, etc.) to obtain the latest location of the most current FAR.

FEDERAL ACQUISITION REGULATION (48 CFR CH. 1)

Clause			Title and Date

52.209-6		Protecting the Government's Interest When Subcontracting with

Contractors Debarred, Suspended, or Proposed for Debarment

(JAN 2005)

52.213-4		Terms and Conditions-Simplified Acquisitions (Other than Commercial

Items) (MAR 2005)

    - 52.222-1                                           Notice to the Government of Labor Disputes (FEB 1997)

52.222-19	Child Labor – Cooperation with Authorities and Remedies (JAN 2004)

    - 52.225-10                                       Notice of Buy American Act/Balance of Payments Program—

Construction Materials  (FEB 2000)

52.225-13		Restrictions on Certain Foreign Purchases (MAR 2005)

52.225-14		Inconsistency Between English Version and Translation of

Contract (AUG 1989)

52.228-3                     Workers’ Compensation Insurance (Defense Base Act);

52.228-4                     Workers’ Compensation and War-Hazard Insurance Overseas (APR 1984)

52.228-5		Insurance - Work on a Government Installation (JAN 1997)

52.228-11 		Pledges of Assets (FEB 1990)

52.228-13		Alternative Payment Protection (JUL 2000)

52.229-6		Taxes - Foreign Fixed-Price Contracts (JUN 2003)

52.232-5		Payments under Fixed-Price Construction Contracts (SEP 2002)

52.232-8		Discounts for Prompt Payment (FEB 2002)

52.232-11		Extras (APR 1984)

52.232-18	Availability of Funds (APR 1984)

52.232-24		Prohibition of Assignment of Claims (JAN 1986)

52.232-27		Prompt Payment for Construction Contracts (OCT 2003)

52.232-34		Payment by Electronic Funds Transfer – Other than Central Contractor Registration (MAY 1999)

52.233-1		Disputes (JUL 2002) Alternate I (DEC 1991)

52.233-3		Protest after Award (AUG 1996)

52.236-2		Differing Site Conditions (APR 1984)

52.236-3		Site Investigation and Conditions Affecting the Work (APR 1984)

52.236-5		Material and Workmanship (APR 1984)

52.236-6		Superintendence by the Contractor (APR 1984)

52.236-7		Permits and Responsibilities (NOV 1991)

52.236-8		Other Contracts (APR 1984)

52.236-9		Protection of Existing Vegetation, Structures,

Equipment, Utilities, and Improvements (APR 1984)

52.236-10		Operations and Storage Areas (APR 1984)

52.236-11		Use and Possession Prior to Completion (APR 1984)

52.236-12		Cleaning Up (APR 1984)

52.236-14		Availability and Use of Utility Services (APR 1984)

52.236-15		Schedules for Construction Contracts (APR 1984)

52.236-21		Specifications and Drawings for Construction  (FEB 1997)

52.236-26 		Preconstruction Conference (FEB 1995)

52.242-14		Suspension Of Work (APR 1984)

52.243-4		Changes (AUG 1987)

52.243-5		Changes and Changed Conditions (APR 1984)

52.244-6		Subcontracts for Commercial Items (MAR 2005)

52.245-4   		Government-Furnished Property (Short Form) (JUN 2003)

52.246-12			  Inspection of Construction (AUG 1996)

52.246-21		Warranty of Construction (APR 1984)

    - 52.249-2                                           Termination for Convenience of the Government (Fixed-Price)

(MAY 2004) Alternate I (APR 1984)

52.249-10 		Default (Fixed-Price Construction) (APR 1984)

The following clauses are set forth in full text:

DEPARTMENT OF STATE ACQUISITION REGULATION (DOSAR) CLAUSES

652.242-73  AUTHORIZATION AND PERFORMANCE (AUG 1999)

(a) The contractor warrants the following:

(1) That is has obtained authorization to operate and do business in the country or countries in which this contract will be performed;

(2) That is has obtained all necessary licenses and permits required to perform this contract; and,

(3) That it shall comply fully with all laws, decrees, labor standards, and regulations of said country or countries during the performance of this contract.

(b) If the party actually performing the work will be a subcontractor or joint venture partner, then such subcontractor or joint venture partner agrees to the requirements of paragraph (a) of

this clause.

652.228-70	INDEMNIFICATION (JULY 1988)

The Contractor expressly agrees to indemnify and to save the Government, its officers, agents, servants, and employees harmless from and against any claim, loss, damages, injury, and liability, however caused, resulting from or arising out of the Contractor's fault or negligence in connection with the performance of work under this contract.  Further, any negligence or alleged negligence of the Government, its officers, agents, servants, or employees, shall not bar a claim for indemnification unless the act or omission of the Government, its officers, agents, servants, or employees is the sole competent, and producing cause of such claim, loss, damages, injury, or liability.

652.243-70  NOTICES (AUG 1999)

Any notice or request relating to this contract given by either party to the other shall be in writing. Said notice or request shall be mailed or delivered by hand to the other party at the address provided in the schedule of the contract. All modifications to the contract must be made in writing by the contracting officer.

652.229-71  PERSONAL PROPERTY DISPOSITION AT POSTS ABROAD (AUG 1999)

Regulations at 22 CFR Part 136 require that U.S. Government employees and their families do not profit personally from sales or other transactions with persons who are not themselves entitled to exemption from import restrictions, duties, or taxes. Should the contractor experience importation or tax privileges in a foreign country because of its contractual relationship to the United States Government, the contractor shall observe the requirements of 22 CFR

Part 136 and all policies, rules, and procedures issued by the chief of mission in that foreign country.

I. LIST OF ATTACHMENTS

ATTACHMENT NO.       DESCRIPTION OF ATTACHMENT            NO.PAGES

Attachment 1   Sample Bank Letter of Guaranty                                  	1

Attachment 2    Breakdown of Price by Divisions                   		1

of Specifications

J. QUOTATION INFORMATION

A.	QUALIFICATIONS OF OFFERORS

Offerors/quoters must be technically qualified and financially responsible to perform the work described in this solicitation.  At a minimum, each Offeror/Quoter must meet the following requirements:

(1)	Be able to understand written and spoken English;

(2)	Have an established business with a permanent address and telephone listing;

(3) 	Be able to demonstrate prior construction experience with suitable references;

(4)	Have the necessary personnel, equipment and financial resources available to perform the work;

(5)	Have all licenses and permits required by local law;

(6) 	Meet all local insurance requirements;

(7) 	Have the ability to obtain or to post adequate performance security, such as bonds, irrevocable letters of credit or guarantees issued by a reputable financial institution;

(8)	Have no adverse criminal record; and

(9)	Have no political or business affiliation which could be considered contrary to the interests of the United States.

B.	SUBMISSION OF QUOTATIONS

This solicitation is for the performance of the construction services described in SCOPE OF WORK, and the Attachments which are a part of this request for quotation.

Each quotation must consist of the following:

Volume                     Title                                                                   No. of Copies*

I  Standard Form 18 including  a completed			___1__

Attachment 4, "BREAKDOWN OF

PROPOSAL PRICE BY DIVISIONS OF SPECIFICATIONS.

II   Performance schedule in the form of a "bar                            ___1____

chart" and Business Management/Technical

Proposal.

Submit the complete quotation to the address indicated on Standard Form 18, if mailed, or the address set forth below, if hand delivered.

American Embassy Kyiv, Ukraine

__________________________________________________

__________________________________________________

__________________________________________________

The Offeror/Quoter shall identify and explain/justify any deviations, exceptions, or conditional assumptions taken with respect to any of the instructions or requirements of this request for quotation in the appropriate volume of the offer.

Volume II: Performance schedule and Business Management/Technical Proposal.

(a)	Present the performance schedule in the form of a "bar chart" indicating when the various portions of the work will be commenced and completed within the required schedule.  This bar chart shall be in sufficient detail to clearly show each segregable portion of work and its planned commencement and completion date.

(b)	The Business Management/Technical Proposal shall be in two parts, including the following information:

Proposed Work Information - Provide the following:

(1) A list of the names, addresses and telephone numbers of the owners, partners, and principal officers of the Offeror;

(2) The name and address of the Offeror's field superintendent for this project;

(3) A list of the names, addresses, and telephone numbers of subcontractors and principal materials suppliers to be used on the project, indicating what portions of the work will be performed by them; and,

(4) Bar chart indicating various portions of the work; when work will commence and be completed in each section.

Experience and Past Performance - List all contracts and subcontracts your company has held over the past three years for the same or similar work.  Provide the following information for each contract and subcontract:

(1) Customer's name, address, and telephone numbers of customer's lead contract and technical personnel;

(2) Contract number and type;

(3) Date of the contract award place(s) of performance, and completion dates; Contract dollar value;

(4) Brief description of the work, including responsibilities; and

(5) Any litigation currently in process or occurring within last 5 years.

C.`52.236-27	SITE VISIT (FEB 1995)

(a)	The clauses at 52.236-2, Differing Site Conditions, and 52.236-3, Site Investigations and Conditions Affecting the Work, will be included in any contract awarded as a result of this solicitation.  Accordingly, offerors or quoters are urged and expected to inspect the site where the work will be performed.

(b)	A site visit has been scheduled for February  20, 11:00 a.m.

(c)	Participants will meet at  6 Pimonenko St., Kyiv, Ukraine

D. `MAGNITUDE OF CONSTRUCTION PROJECT

It is anticipated that the range in price of this contract will be:

between 25,000.00 USD and 100, 000.00

# LATE QUOTATIONS.  Late quotations shall be handled in accordance with FAR

F.  52.252-1 SOLICITATION PROVISIONS INCORPORATED BY REFERENCE (FEB 1998)

This contract incorporates the following provisions by reference, with the same force and effect as if they were given in full text.  Upon request, the Contracting Officer will make their full text available.  The offeror is cautioned that the listed provisions may include blocks that must be completed by the offeror and submitted with its quotation or offer.  In lieu of submitting the full text of those provisions, the offeror may identify the provision by paragraph identifier and provide the appropriate information with its quotation or offer.  Also, the full text of a solicitation provision may be accessed electronically at:

http://www.arnet.gov/far/   or,   http://farsite.hill.af.mil/search.htm

These addresses are subject to change.  If the Federal Acquisition Regulation (FAR) is not available at the locations indicated above, use of an Internet "search engine" (such as, Yahoo, Infoseek, Alta Vista, etc.) is suggested to obtain the latest location of the most current FAR.

http://www.statebuy.gov/home.htm

FEDERAL ACQUISITION REGULATION (48 CFR CH. 1)

## 52.215-1 INSTRUCTIONS TO OFFERORS--COMPETITIVE ACQUISITION (JAN 2004), which is incorporated by reference into this solicitation. K. EVALUATION CRITERIA

Award will be made to the lowest priced, acceptable, responsible quoter.  The Government reserves the right to reject quotations that are unreasonably low or high in price.

The Government will determine acceptability by assessing the offeror's compliance with the terms of the RFQ.  The Government will determine responsibility by analyzing whether the apparent successful quoter complies with the requirements of FAR 9.1, including:

-          ability to comply with the required performance period, taking into consideration all existing commercial and governmental business commitments;

-          satisfactory record of integrity and business ethics;

-          necessary organization, experience, and skills or the ability to obtain them;

-          necessary equipment and facilities or the ability to obtain them; and

-          otherwise qualified and eligible to receive an award under applicable laws and regulations.

SECTION L - REPRESENTATIONS, CERTIFICATIONS AND OTHER

STATEMENTS OF OFFERORS OR QUOTERS

L.1	52.204-3 TAXPAYER IDENTIFICATION (OCT 1998)

(a) Definitions.

"Common parent", as used in this provision, means that corporate entity that owns or controls an affiliated group of corporations that files its Federal income tax returns on a consolidated basis, and of which the offeror is a member.

"Taxpayer Identification Number (TIN)", as used in this provision, means the number required by the IRS to be used by the offeror in reporting income tax and other returns.  The TIN may be either a Social Security Number or an Employer Identification Number.

(b) All offerors must submit the information required in paragraphs (d)through (f) of this provision in order to comply with debt collection requirements of 31 U.S.C. 7701(c) and 3325 (d), reporting requirements of 26 USC 6041, 6041A, and 6050M and implementing regulations issued by the Internal Revenue Service (IRS).  If the resulting contract is subject to the reporting requirements described in FAR 4.904, the failure or refusal by the offeror to furnish the information may result in a 31 percent reduction of payments otherwise due under the contract.

(c) The TIN may be used by the Government to collect and report on any delinquent amounts arising out of the offeror’s relationship with the Government (3l USC 7701( c)(3)).  If the resulting contract is subject to the payment reporting requirements described in FAR 4.904, the TIN provided hereunder may be matched with IRS records to verify the accuracy of the offeror’s TIN.

(d) Taxpayer Identification Number (TIN).

TIN: ____________________________

___ TIN has been applied for.

___ TIN is not required because:

__  Offeror is a nonresident alien, foreign corporation, or foreign partnership that does not have income effectively connected with the conduct of a trade or business in the U.S. and does not have an office or place of business or a fiscal paying agent in the U.S.;

__ Offeror is an agency or instrumentality of a foreign government;

__ Offeror is an agency or instrumentaltiy of the Federal Government.

(e) Type of Organization.

__ Sole Proprietorship;

__ Partnership:

__ Corporate Entity (not tax exempt);

__ Corporate Entity (tax emempt);

__  Government entity (Federal, State, or local);

__   Foreign government;

__   International organization per 26 CFR 1.6049-4;

__   Other ___________________________________________

(f) Common Parent.

___  Offeror is not owned or controlled by a common parent as defined in paragraph (a) of this clause.

___ Name and TIN of common parent;

Name _______________________________________________

TIN ________________________________________________

(End of provision)

L.2	52.204-6  CONTRACTOR IDENTIFICATION NUMBER -DATA UNIVERSAL NUMBERING SYSTEM (DUNS) NUMBER (OCT 2003)

(a)	The offeror shall enter, in the block with its name and address on the cover page of its offer, the annotation “DUNS” or “DUNS+4” followed by the DUNS number or DUNS+4 that identifies the offeror’s name and address exactly as stated in the offer.  The DUNS number if a nine-digit number assigned by Dun and Bradstreet Information Services.  The DUNS+4 is the DUNS number plus a 4-character suffix that may be assigned at the discretion of the offeror to establish additional CCR records for identifying alternative Electronic Funds Transfer (EFT) accounts (see Subpart 32.11) for the same parent company.

If the offeror does not have a DUNS number, it should contact Dun and Bradstreet directly to obtain one.

An offeror may obtain a DUNS number-

If located within the United States, by calling Dun and Bradstreet at 1-866-705-5711 or via the Internet at http://www.dnb.com; or

If located outside the United States, by contacting the local Dun and Bradstreet office.

(2) The offeror should be prepared to provide the following information:

Company legal business name.

Tradestyle, doing business, or other name by which your entity is commonly recognized.

Company physical street address, city, state and Zip Code.

Company mailing address, city, state and Zip Code (if separate from physical)

Company telephone number

Date the company was started.

Number of employees at your location.

Chief executive officer/key manager.

Line of business (industry)

Company Headquarters name and address (reporting relationship within your entity).

L.3     52.204-8   ANNUAL REPRESENTATIONS AND CERTIFICATIONS

(JAN 2005)

(a)(1) If the clause at 52.204–7, Central Contractor Registration, is included in this solicitation, paragraph (b) of this provision applies.

(2) If the clause at 52.204–7 is not included in this solicitation, and the offeror is currently registered in CCR, and has completed the ORCA electronically, the offeror may choose to use paragraph (b) of this provision instead of completing the corresponding individual representations and certifications in the solicitation. The offeror shall indicate which option applies by checking one of the following boxes:

[ ] (i) Paragraph (b) applies.

[ ] (ii) Paragraph (b) does not apply and the offeror has completed the individual representations and certifications in the solicitation.

(b) The offeror has completed the annual representations and certifications electronically via the Online Representations and Certifications Application (ORCA) website at http://orca.bpn.gov. After reviewing the ORCA database information, the offeror verifies by submission of the offer that the representations and certifications currently posted electronically have been entered or updated within the last 12 months, are current, accurate, complete, and applicable to this solicitation (including the business size standard applicable to the NAICS code referenced for this solicitation), as of the date of this offer and are incorporated in this offer by reference (see FAR 4.1201); except for the changes identified below

[offeror to insert changes, identifying change by clause number, title, date].

These amended representation(s) and/or certification(s) are also incorporated in this offer and are current, accurate, and complete as of the date of this offer.

| FAR Clause # | Title | Date | Change |
| --- | --- | --- | --- |

Any changes provided by the offeror are applicable to this solicitation only, and do not result in an update to the representations and certifications posted on ORCA.

L.4	AUTHORIZED CONTRACT ADMINISTRATOR

If the offeror does not fill-in the blanks below, the official who signed the offer will be deemed to be the offeror's representative for Contract Administration, which includes all matters pertaining to payments.

Name:    _________________________________________________

Address: _________________________________________________

_________________________________________________

Telephone Number: ________________________________________

L.5	DEFENSE BASE ACT INSURANCE – COVERED CONTRACTOR EMPLOYEES

(a)  Bidders/Offerors shall indicate below whether or not any of the following categories of employees will be employed on the resultant contract, and, if so, the number of such employees:

| Category | Yes/No | Number |
| --- | --- | --- |
| (1) United States citizens or residents |  |  |
| (2) Individuals hired in the United States, regardless of citizenship |  |  |
| (3) Local nationals or third country nationals where contract performance takes place in a country where there are no local workers’ compensation laws |  | Local nationals: ______________ Third Country Nationals: _____________ |
| (4) Local nationals or third country nationals where contract performance takes place in a country where there are local workers’ compensation laws |  | Local nationals: ______________ Third Country Nationals: _____________ |

(b)  If the bidder/offeror has indicated “yes” in block (a)(4) of this provision, the bidder/offeror shall submit, as part of its offer, a statement that indicates that such local nationals and/or third country nationals will be provided workers’ compensation coverage against the risk of work injury or death under a local workers’ compensation law.  For those employees, the bidder/offeror shall also assume liability toward the employees and their beneficiaries for war-hazard injury, death, capture, or detention, in accordance with the clause at FAR 52.228-4.

(c)  If the bidder/offeror has indicated “yes” in blocks (a)(1), (2), or (3) of this provision, the bidder/offeror shall compute Defense Base Act insurance costs covering those employees pursuant to the terms of the contract between the Department of State and the Department’s Defense Base Act insurance carrier at the rates specified in DOSAR 652.228-74.  If DOSAR provision 652.228-74 is not included in this solicitation, the bidder/offeror shall notify the contracting officer before the closing date so that the solicitation can be amended accordingly.

ATTACHMENT #1

SAMPLE LETTER OF BANK GUARANTY

Place [         ]

Date [          ]

Contracting Officer

U.S. Embassy, [Post name]

[Mailing Address]

Letter of Guaranty No. _______

SUBJECT: Performance and Guaranty

The Undersigned, acting as the duly authorized representative of the bank, declares that the bank hereby guarantees to make payment to the Contracting Officer by check made payable to the Treasurer of the United States, immediately upon notice, after receipt of a simple written request from the Contracting Officer, immediately and entirely without any need for the Contracting Officer to protest or take any legal action or obtain the prior consent of the Contractor to show any other proof, action, or decision by an other authority, up to the sum of [Amount equal to 20% of the contract price in U.S. dollars during the period ending with the date of final acceptance and 10% of the contract price during contract guaranty period], which represents the deposit required of the contractor to guarantee fulfillment of his obligations for the satisfactory, complete, and timely performance of the said contract [contract number] for [description of work] at [location of work] in strict compliance with the terms, conditions and specifications of said contract, entered into between the Government and [name of contractor] of [address of contractor] on [contract date], plus legal charges of 10% per annum on the amount called due, calculated on the sixth day following receipt of the Contracting Officer’s written request until the date of payment.

The undersigned agrees and consents that said contract may be modified by Change Order or Supplemental Agreement affecting the validity of the guaranty provided, however, that the amount of this guaranty shall remain unchanged.

The undersigned agrees and consents that the Contracting Officer may make repeated partial demands on the guaranty up to the total amount of this guaranty, and the bank will promptly honor each individual demand.

This letter of guaranty shall remain in effect until 3 months after completion of the guaranty period of Contract requirement.

————————————————————————————————-

Depository Institution: [Name]

Address:					Location: ______________

Representative(s): ___________  ___________	State of Inc.: ____________

___________  ___________	Corporate Seal:

___________  ___________

————————————————————————————————

Certificate of Authority is attached evidencing authority of the signer to bind the bank to this document.

ATTACHMENT #2

UNITED STATES DEPARTMENT OF STATE

BREAKDOWN OF PRICE BY DIVISIONS OF SPECIFICATIONS

(1)DIVISION/DESCRIPTION     (2)LABOR       (3)MATERIALS     (4)OVERHEAD     (5)PROFIT   (6)TOTAL

1  General Requirements

2.  Site Work

3.  Concrete

4.  Masonry

5.  Metals

6.  Wood and Plastic

7.  Thermal and Moisture

8.  Doors and Windows

9.  Finishes

10. Specialties

11. Equipment

12  Furnishings

13. Special Construction

14. Conveying Systems

15. Mechanical

16. Electrical

TOTAL:    in USD

Allowance Items:

PROPOSAL PRICE TOTAL:  in USD

Alternates  (list separately do not total)

Offeror:                                                                                                         Date

PRICE BREAKDOWN BY DIVISION OF SPECIFICATION ITEMS