## 25F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 001R2
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6554.5193
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -2662.36 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | -2530.98 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | -2533.19 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1617.98 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | -2530.98 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2942.68 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1367.72 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2892.12 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 1466.33 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2785.89 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 1617.98 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | -2533.19 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2927.46 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1466.33 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2935.21 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2935.21 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2942.68 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2884.67 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2883.26 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 2779.9 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2884.67 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | -2662.36 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2892.12 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1367.72 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2774.48 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2927.46 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2779.9 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2883.26 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 2785.89 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2774.48 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 001R2
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6418.7893
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -1819.64 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | -1715.26 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | -1801.23 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1747.67 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | -1715.26 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2939.25 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1516.42 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2904.5 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 1635.36 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2815.38 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 1747.67 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | -1801.23 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2931.11 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1635.36 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2932.7 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2932.7 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2939.25 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2904.68 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2896.55 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 2796.43 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2904.68 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | -1819.64 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2904.5 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1516.42 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2797.92 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2931.11 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2796.43 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2896.55 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 2815.38 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2797.92 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 001R2
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 5981.284
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -1867.61 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | -1687.53 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | -1767.46 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1635.86 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | -1687.53 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2850.14 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1408.46 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2924.05 | N-2: Monroe - Custer #1&2 500kV | Branch PORTALWY (42001) TO VISTA P (42087) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 1526.38 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2821.9 | N-2: Monroe - Custer #1&2 500kV | Branch PORTALWY (42001) TO VISTA P (42087) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 1635.86 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | -1767.46 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2846.57 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1526.38 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2843.73 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2843.73 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2850.14 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2916.46 | N-2: Monroe - Custer #1&2 500kV | Branch PORTALWY (42001) TO VISTA P (42087) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2915.39 | N-2: Monroe - Custer #1&2 500kV | Branch PORTALWY (42001) TO VISTA P (42087) CKT 1 [115.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 2823.87 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2916.46 | N-2: Monroe - Custer #1&2 500kV | Branch PORTALWY (42001) TO VISTA P (42087) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | -1867.61 | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2924.05 | N-2: Monroe - Custer #1&2 500kV | Branch PORTALWY (42001) TO VISTA P (42087) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1408.46 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2815.02 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2846.57 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2823.87 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2915.39 | N-2: Monroe - Custer #1&2 500kV | Branch PORTALWY (42001) TO VISTA P (42087) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 2821.9 | N-2: Monroe - Custer #1&2 500kV | Branch PORTALWY (42001) TO VISTA P (42087) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2815.02 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 001R2
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4946.6607
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1815.85 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2037.19 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1942.42 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2723.15 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2037.19 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2982.03 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 2610.42 | N-1: Custer - Sedro NT 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2904.13 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2710.66 | N-1: Custer - Sedro NT 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2773.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2723.15 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1942.42 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2978.43 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 2710.66 | N-1: Custer - Sedro NT 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2983.41 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2983.41 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2982.03 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2899.76 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2899.39 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2771.18 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2899.76 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1815.85 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2904.13 | N-2: Monroe - Custer #1&2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2610.42 | N-1: Custer - Sedro NT 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2765.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2978.43 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2771.18 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2899.39 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2773.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2765.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 001R2
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4627.416
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2087.25 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2285.24 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2195.4 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2738.45 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2285.24 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3009.64 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 2726.93 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2849.61 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2733.98 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2714.95 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2738.45 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2195.4 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3004.03 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 2733.98 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3003.82 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3003.82 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3009.64 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2839.59 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2836.66 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2701.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2839.59 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2087.25 | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2849.61 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2726.93 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2677.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3004.03 | N-2: Monroe - Custer #1&2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2701.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2836.66 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2714.95 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2677.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
G0 | -2662.36 | -1819.64 | -1867.61 | 1815.85 | 2087.25
G1 | -2533.19 | -1801.23 | -1767.46 | 1942.42 | 2195.4 | Season/Year: | WINTER 2009
G2 | -2530.98 | -1715.26 | -1687.53 | 2037.19 | 2285.24 | Direction: | North-to-South (NS)
G3 | 1367.72 | 1516.42 | 1408.46 | 2610.42 | 2726.93 | Case Loads: | Heavy Loads
G4 | 1466.33 | 1635.36 | 1526.38 | 2710.66 | 2733.98 | Outage: | 001R2
G5 | 1617.98 | 1747.67 | 1635.86 | 2723.15 | 2738.45 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2927.46 | 2931.11 | 2846.57 | 2978.43 | 3004.03 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2935.21 | 2932.7 | 2843.73 | 2983.41 | 3003.82 | Study Person: | FRP9899
G8 | 2942.68 | 2939.25 | 2850.14 | 2982.03 | 3009.64 | Source: | 001R2WINTER09v5NSH
G9 | 2883.26 | 2896.55 | 2915.39 | 2899.39 | 2836.66
G10 | 2884.67 | 2904.68 | 2916.46 | 2899.76 | 2839.59
G11 | 2892.12 | 2904.5 | 2924.05 | 2904.13 | 2849.61
G12 | 2774.48 | 2797.92 | 2815.02 | 2765.42 | 2677.26
G13 | 2779.9 | 2796.43 | 2823.87 | 2771.18 | 2701.6
G14 | 2785.89 | 2815.38 | 2821.9 | 2773.2 | 2714.95
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 001R2 | Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6554.5193 | -2662.36 | -2533.19 | -2530.98 | 1367.72 | 1466.33 | 1617.98 | 2927.46 | 2935.21 | 2942.68 | 2883.26 | 2884.67 | 2892.12 | 2774.48 | 2779.9 | 2785.89
35F | 6418.7893 | -1819.64 | -1801.23 | -1715.26 | 1516.42 | 1635.36 | 1747.67 | 2931.11 | 2932.7 | 2939.25 | 2896.55 | 2904.68 | 2904.5 | 2797.92 | 2796.43 | 2815.38
45F | 5981.284 | -1867.61 | -1767.46 | -1687.53 | 1408.46 | 1526.38 | 1635.86 | 2846.57 | 2843.73 | 2850.14 | 2915.39 | 2916.46 | 2924.05 | 2815.02 | 2823.87 | 2821.9
60F | 4946.6607 | 1815.85 | 1942.42 | 2037.19 | 2610.42 | 2710.66 | 2723.15 | 2978.43 | 2983.41 | 2982.03 | 2899.39 | 2899.76 | 2904.13 | 2765.42 | 2771.18 | 2773.2
70F | 4627.416 | 2087.25 | 2195.4 | 2285.24 | 2726.93 | 2733.98 | 2738.45 | 3004.03 | 3003.82 | 3009.64 | 2836.66 | 2839.59 | 2849.61 | 2677.26 | 2701.6 | 2714.95

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -2660.38 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | 2.98 | 467.04 | 468.64 | 6597.18 | -2662.36 | -1717.42 | FULL
G1 | -2531.42 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | 2.98 | 470.48 | 470.57 | 6522.18 | -2533.19 | -1598.72 | FULL
G2 | -2530.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | 2.98 | 471.55 | 469.35 | 6525.49 | -2530.98 | -1566.41 | FULL
G3 | 1369.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 484.14 | 484.08 | 6554.27 | 1367.72 | 672.48 | FULL
G4 | 1469.12 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 484.58 | 484.53 | 6486.02 | 1466.33 | 755.52 | FULL
G5 | 1622.54 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 486.18 | 485.97 | 6500.14 | 1617.98 | 877.56 | FULL
G6 | 2941.35 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 490.25 | 489.88 | 6590.2 | 2927.46 | 1642.39 | FULL
G7 | 2950.07 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 490.47 | 490.15 | 6523 | 2935.21 | 1676.74 | FULL
G8 | 2956.7 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 490.44 | 490.11 | 6537.56 | 2942.68 | 1709.2 | FULL
G9 | 2897.91 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -16.96 | -191.65 | -140.43 | 6613.19 | 2883.26 | 1802.27 | FULL
G10 | 2899.67 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -11.42 | -108.75 | -139.67 | 6546.59 | 2884.67 | 1832.15 | FULL
G11 | 2907.2 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -16.96 | -191.31 | -140.36 | 6561.91 | 2892.12 | 1871.33 | FULL
G12 | 2788.57 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -11.42 | -101.99 | -139.77 | 6625.33 | 2774.48 | 1873.89 | FULL
G13 | 2793.57 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -16.96 | -184.69 | -140.42 | 6559.46 | 2779.9 | 1903.88 | FULL
G14 | 2799.92 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -11.42 | -101.72 | -139.48 | 6575.27 | 2785.89 | 1940.26 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -1819.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | 2.98 | 469.02 | 469.06 | 6447.78 | -1819.64 | -1209.61 | FULL
G1 | -1801.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | 2.98 | 467.92 | 467.83 | 6375.26 | -1801.23 | -1152.3 | FULL
G2 | -1715.42 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | 2.98 | 468.13 | 468.1 | 6380.3 | -1715.26 | -1089.27 | FULL
G3 | 1520.63 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 477.02 | 476.86 | 6420.13 | 1516.42 | 780.66 | FULL
G4 | 1638.42 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 477.52 | 477.36 | 6352.72 | 1635.36 | 877.85 | FULL
G5 | 1752.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 478.05 | 477.9 | 6367.35 | 1747.67 | 970.95 | FULL
G6 | 2943.93 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 480.87 | 480.45 | 6456.15 | 2931.11 | 1680.19 | FULL
G7 | 2946.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 481.1 | 480.74 | 6389.27 | 2932.7 | 1715.18 | FULL
G8 | 2952.85 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 481.13 | 480.77 | 6404.34 | 2939.25 | 1746.58 | FULL
G9 | 2910.4 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -11.42 | -108.89 | -133.87 | 6479.94 | 2896.55 | 1842.34 | FULL
G10 | 2919.22 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -16.96 | -187.05 | -129.6 | 6414.21 | 2904.68 | 1879.68 | FULL
G11 | 2919.47 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -11.42 | -108.74 | -133.93 | 6430.14 | 2904.5 | 1890.27 | FULL
G12 | 2811.66 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -16.96 | -185.56 | -135.21 | 6492.55 | 2797.92 | 1922.6 | FULL
G13 | 2810.28 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -11.42 | -102.11 | -134.34 | 6427.89 | 2796.43 | 1934.83 | FULL
G14 | 2829.31 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -16.96 | -185.85 | -134.9 | 6443.81 | 2815.38 | 1972.28 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -1866.29 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | 2.98 | 437.36 | 437.31 | 6015.46 | -1867.61 | -1221.22 | FULL
G1 | -1766.36 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | 2.98 | 437.89 | 437.86 | 5940.45 | -1767.46 | -1132.98 | FULL
G2 | -1686.78 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3159 Sedro-Belling 230kV & Sedro 230/115kV Bk#1 | 2.98 | 437.7 | 437.66 | 5949.55 | -1687.53 | -1051.07 | FULL
G3 | 1409.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 442.28 | 442.34 | 5979.11 | 1408.46 | 741.11 | FULL
G4 | 1529.36 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 442.95 | 442.79 | 5911.73 | 1526.38 | 838.07 | FULL
G5 | 1639.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 443.43 | 443.35 | 5926.76 | 1635.86 | 929.21 | FULL
G6 | 2858.47 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 446.23 | 445.9 | 6016.11 | 2846.57 | 1657.63 | FULL
G7 | 2856.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 445.34 | 445.07 | 5949.27 | 2843.73 | 1676.69 | FULL
G8 | 2862.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 445.54 | 445.06 | 5964.63 | 2850.14 | 1708.32 | FULL
G9 | 2929.9 | Branch PORTALWY (42001) TO VISTA P (42087) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 16.96 | 205.73 | 165.48 | 6043.32 | 2915.39 | 1868.34 | FULL
G10 | 2932.07 | Branch PORTALWY (42001) TO VISTA P (42087) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 11.42 | 121.98 | 166.72 | 5976.99 | 2916.46 | 1895.37 | FULL
G11 | 2939.23 | Branch PORTALWY (42001) TO VISTA P (42087) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 11.42 | 121.87 | 166.03 | 5993.44 | 2924.05 | 1928.43 | FULL
G12 | 2828.12 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -16.96 | -175.83 | -129.09 | 6055.17 | 2815.02 | 1956.35 | FULL
G13 | 2837.24 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -16.96 | -185.9 | -129.24 | 5990.29 | 2823.87 | 1987.34 | FULL
G14 | 2835.83 | Branch PORTALWY (42001) TO VISTA P (42087) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 16.96 | 198.75 | 165.88 | 6006.98 | 2821.9 | 2013.41 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1820.43 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 444.16 | 444.08 | 4941.44 | 1815.85 | 1027.01 | FULL
G1 | 1948.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 445.49 | 445.36 | 4876.95 | 1942.42 | 1114.7 | FULL
G2 | 2042.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 445.11 | 445.09 | 4894.1 | 2037.19 | 1208.43 | FULL
G3 | 2619.74 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Custer - Sedro NT 230kV | 9.43 | 447.42 | 447.49 | 4960.9 | 2610.42 | 1516.34 | FULL
G4 | 2721.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Custer - Sedro NT 230kV | 9.43 | 447.42 | 447.49 | 4898.63 | 2710.66 | 1600.66 | FULL
G5 | 2734.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 445.67 | 445.26 | 4916.91 | 2723.15 | 1643.38 | FULL
G6 | 2992.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 445.59 | 445.23 | 4985.54 | 2978.43 | 1811.92 | FULL
G7 | 2997.72 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 444.94 | 444.53 | 4920.38 | 2983.41 | 1857.05 | FULL
G8 | 2996.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 443.66 | 443.14 | 4937.64 | 2982.03 | 1869.74 | FULL
G9 | 2912.52 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.82 | -468.63 | -468.25 | 5006.51 | 2899.39 | 1944.8 | FULL
G10 | 2913.08 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -11.42 | -100.87 | -119.14 | 4942.39 | 2899.76 | 1973.16 | FULL
G11 | 2918.48 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | -16.96 | -174.46 | -120.45 | 4960.34 | 2904.13 | 2004.83 | FULL
G12 | 2776.67 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.78 | -468.41 | -469.35 | 5022 | 2765.42 | 2013.09 | FULL
G13 | 2782.74 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.78 | -469.51 | -472.46 | 4958.59 | 2771.18 | 2036.64 | FULL
G14 | 2784.89 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.82 | -468.32 | -465.99 | 4977.59 | 2773.2 | 2064.95 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2093.12 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 444.98 | 445.2 | 4624.5 | 2087.25 | 1197.23 | FULL
G1 | 2202.88 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 445.66 | 445.22 | 4561.14 | 2195.4 | 1287.2 | FULL
G2 | 2294.3 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 3153 Murr-Cust-Sedro & Sedro-Fredonia 230kV | 8.57 | 445.1 | 445.13 | 4579.54 | 2285.24 | 1374.07 | FULL
G3 | 2738.01 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 444.47 | 444.04 | 4644.01 | 2726.93 | 1617.37 | FULL
G4 | 2745.18 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 444.68 | 444.27 | 4580.95 | 2733.98 | 1648.37 | FULL
G5 | 2749.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 444.24 | 443.79 | 4597.6 | 2738.45 | 1679.34 | FULL
G6 | 3018.69 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 444.93 | 444.54 | 4665.66 | 3004.03 | 1864.5 | FULL
G7 | 3019.08 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 444.7 | 444.27 | 4601.78 | 3003.82 | 1895.63 | FULL
G8 | 3023.9 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Monroe - Custer #1&2 500kV | 36.64 | 444.81 | 444.41 | 4619.99 | 3009.64 | 1925.79 | FULL
G9 | 2849.13 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.78 | -454.54 | -454.84 | 4683.69 | 2836.66 | 1953.4 | FULL
G10 | 2852.17 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.78 | -454.91 | -455.29 | 4619.87 | 2839.59 | 1981.37 | FULL
G11 | 2861.73 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.78 | -453.17 | -454.9 | 4638.62 | 2849.61 | 2016.25 | FULL
G12 | 2688.25 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.78 | -456.86 | -456.54 | 4699.6 | 2677.26 | 1994.8 | FULL
G13 | 2713.02 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.78 | -457.95 | -457.57 | 4637.54 | 2701.6 | 2044.06 | FULL
G14 | 2727.17 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.78 | -458 | -457.48 | 4656.75 | 2714.95 | 2078.12 | FULL
001R2WINTER09v5NSH