## Introduction
Hanford Electrical Safety Program Arc Flash Calculator
This Excel file combines arc flash equations from a proposal to NFPA 70E-2003 with simplified equations to calculate available fault current. This tool uses methods that have been shown to result in conservative estimates of fault current, which should result in conservative estimates of arc incident energy if appropriate arc fault clearing times are used. An IEEE 1584 equation is used to calculate arcing fault current. That is the fault current value that is used to determine the clearing time of the overcurrent protective device ahead of the potential arc fault location. Electrical engineering should be consulted to obtain information on fault clearing times.
This spreadsheet is not intended to replace existing up to date fault studies or support of experienced electrical engineers, but is one tool that can assist engineers, planners, and electrical safety POCs in performing a flash hazard analysis. Arc flash calculation is not an exact science and caution is always necessary, including use of multiple alternate methods that are available to verify results and ensure the highest level of safety based on the best information available.
According to the NFPA 70E Technical Committee on Electrical Safety Requirements for Employee Workplaces, “This proposal presents the best information available to date on arc fault hazards. Public review and comments are strongly encouraged. Recent testing has enabled development of improved equations for calculating the arc flash incident energy at the arc flash boundary. While the testing and development of methods is not complete this proposal contains methods that reflect significantly more laboratory data than the existing methods and will allow improved safety.”
 | This calculator is for use only with systems operating at less than 1000 volts. If any doubts exist on use of this spreadsheet, or to perform a flash hazard analysis on systems operating at more than 1000 volts, consult with an electrical engineer or other knowledgeable person. | 
Question/comments? Contact Electrical Safety (371-7886)

## Calculator
Short Circuit and Arc Flash Calculator |  |  |  |  | Arc-In-Box energy = cal/cm2 at specified working distance |  |  |  |  | K = constant for arc in a box (see Arc Calc Info page for equations)
| (<1000 volts only) |  |  |  |  | Flash Protection Boundary (inches) where |  |  |  | Electrode gap, 25mm = 1 inch
Transformer |  | Input: |  |  |  | arc incident energy = 1.2 cal/cm2 |  |  |  | Log (IIA) for less than 1 kV (calculated)
| Xfmr KVA: | [6 empty] | Enter working distance (inches): | 18
| Xfmr Secondary Line to Line Volts: |  |  | Xfmr FLA = |  |  |  | Arc-In-Box Incident Energy: |  | Log (IBF) | K | Gap (mm) | Log (IIA) | Volts > kV | Amps > kA
| Xfmr impedance %: |  |  | Xfmr 3-Ph ISC (Amps)= |  |  |  | Flash Protection Boundary: |  | #VALUE! | -0.097 | 25 | #VALUE! | 0 | #VALUE!
| Fault Clearing Time (seconds): |  | @ | arc fault current (Amps)
Conductors per phase:
Feeder | (S)ingle conductors or (C)able: | [6 empty] | Enter working distance (inches): | 18
| AL or CU: | [6 empty] | Arc-In-Box Incident Energy:
| Conductor length: | [6 empty] | Flash Protection Boundary: | [6 empty] | Amps > kA
| Conductor AWG or kcmil |  |  | Isc at fault (Amps) = | [5 empty] | #VALUE! |  |  | #VALUE! |  | #VALUE!
| Magnetic conduit (Y or N): | [10 empty] | "f" | "M"
| Fault Clearing Time (seconds): |  | @ | arc fault current (Amps) | [7 empty] | FALSE | 1
Isc at beginning of circuit (Amps):
Branch Circuit | Conductors per phase: | [6 empty] | Enter working distance (inches): | 18
| (S)ingle conductors or (C)able: | [6 empty] | Arc-In-Box Incident Energy: | 0
| AL or CU: | [6 empty] | Flash Protection Boundary: | 0
| Conductor length: | [13 empty] | Amps > kA
| Conductor AWG or kcmil: |  |  | Isc at fault (Amps) = | 0 |  |  |  |  | #NUM! |  |  | #NUM! |  | 0
| Metallic conduit? (Y or N): | [5 empty] | Scroll down to enter equipment ID information |  |  |  |  | "f" | "M"
| Fault Clearing Time (seconds): |  | @ | arc fault current (Amps) | [8 empty] | 1
Flash Calculation Location:
Transformer ID:
Panel ID:
Branch Circuit ID:
Other Equipment ID:
Note on C7: Contact Electrical Safety to obtain fault clearing times
Note on C15: Contact Electrical Safety to obtain fault clearing times
Note on C24: Contact Electrical Safety to obtain fault clearing times

## "C" Values
Three single conductors, 600-volt | [5 empty] | Three-conductor cable, 600-volt
AWG or | Copper Conductors |  | AWG or | Aluminum Conductors |  | AWG or | Copper Conductors |  | AWG or | Aluminum Conductors
kcmil | Conduit |  | kcmil | Conduit |  | kcmil | Conduit |  | kcmil | Conduit
| Steel | Nonmagnetic |  | Steel | Nonmagnetic |  | Steel | Nonmagnetic |  | Steel | Nonmagnetic
14 | 389 | 389 | 14 | 236 | 236 | 14 | 389 | 389 | 14 | 236 | 236
12 | 617 | 617 | 12 | 375 | 375 | 12 | 617 | 617 | 12 | 375 | 375
10 | 981 | 981 | 10 | 598 | 598 | 10 | 981 | 981 | 10 | 598 | 598
8 | 1557 | 1558 | 8 | 951 | 951 | 8 | 1559 | 1559 | 8 | 951 | 951
6 | 2425 | 2430 | 6 | 1480 | 1481 | 6 | 2431 | 2433 | 6 | 1481 | 1482
4 | 3806 | 3825 | 4 | 2345 | 2350 | 4 | 3830 | 3837 | 4 | 2351 | 2353
3 | 4760 | 4802 | 3 | 2948 | 2958 | 3 | 4760 | 4802 | 3 | 2948 | 2958
2 | 5906 | 6044 | 2 | 3713 | 3729 | 2 | 5989 | 6087 | 2 | 3733 | 3739
1 | 7292 | 7493 | 1 | 4645 | 4678 | 1 | 7454 | 7579 | 1 | 4686 | 4699
1/0 | 8924 | 9317 | 1/0 | 5777 | 5838 | 1/0 | 9209 | 9472 | 1/0 | 5852 | 5875
2/0 | 10755 | 11423 | 2/0 | 7186 | 7301 | 2/0 | 11244 | 11703 | 2/0 | 7327 | 7372
3/0 | 12843 | 13923 | 3/0 | 8826 | 9110 | 3/0 | 13656 | 14410 | 3/0 | 9077 | 9242
4/0 | 15082 | 16673 | 4/0 | 10740 | 11174 | 4/0 | 16391 | 17482 | 4/0 | 11184 | 11408
250 | 16483 | 18593 | 250 | 12122 | 12862 | 250 | 18310 | 19779 | 250 | 12796 | 13236
300 | 18176 | 20867 | 300 | 13909 | 14922 | 300 | 20617 | 22524 | 300 | 14916 | 15494
350 | 19703 | 22736 | 350 | 15484 | 16812 | 350 | 22646 | 24904 | 350 | 15413 | 17635
400 | 20565 | 24296 | 400 | 16670 | 18505 | 400 | 24253 | 26915 | 400 | 18461 | 19587
500 | 22185 | 26706 | 500 | 18755 | 21390 | 500 | 26980 | 30028 | 500 | 21394 | 22987
600 | 22965 | 28033 | 600 | 20093 | 23451 | 600 | 28752 | 32236 | 600 | 23633 | 25750
750 | 24136 | 28303 | 750 | 21766 | 25976 | 750 | 31050 | 32404 | 750 | 26431 | 29036
1000 | 25278 | 31490 | 1000 | 23477 | 28778 | 1000 | 33864 | 37197 | 1000 | 29864 | 32938
| 244828 | 280499 |  | 192096 | 213475 |  | 284982 | 307338 |  | 213707 | 227951

## Isc Info
Source (except as noted): |  | Bulletin EPR-1, Electrical Plan Review
Cooper Bussman, May 2000
Pages 8 - 10
http://www.bussmann.com/library/docs/EPR_Booklet.pdf
Xfmr FLA = | (KVA * 1000) / (EL-L * 1.732)
*3-Ph ISC at xfmr = | (((KVA / 1000) * 106) / (1.732 * EL-L)) * 100 / Z%) |  | (*NFPA 70E, 2000 Edition, Appendix B, Section B-2-1)
"f" factor = | (1.73 * L * IL-L-L) / (C * EL-L)
"M" = | 1/(1 + f)
3-Ph Isc at fault = | ISC at xfmr * M
where:
EL-L = phase-to-phase voltage
Z = transformer nameplate impedance, in percent
L = length of conductor to the fault
IL-L-L = available 3-phase short circuit current at beginning of circuit
C = constant from "C" Values sheet (multiply by number of conductors per phase for parallel runs)
"f" factor = calculated variable from source document formula
M = calculated variable from source document formula

## Arc Calc Info
References:
“The Other Electrical Hazard: Electrical Arc Blast Burns,” R. Lee, IEEE Trans. Industrial Applications, Vol 1A-18. No. 3, Page 246, May/June 1982.
“The Use of Low Voltage Current Limiting Fuses to Reduce Arc Flash Energy,” T. Neal, V. Saporita, T. Macalady, R. Doughty, K. Borgwald, Record of Conference Papers IEEE PCIC-99-36.
“Predicting Incident Energy to Better Manage the Electric Arc Hazard on 600 V Power Distribution Systems,” R. L. Doughty, T. E. “Testing Update on Protective Clothing & Equipment For Electric Arc Exposure, R. Doughty, T. Neal, T. Dear, A. Bingham, Record of Conference Papers IEEE PCIC-97-35.
“Testing Update on Protective Clothing & Equipment For Electric Arc Exposure, R. Doughty, T. Neal, T. Dear, A. Bingham, Record of Conference Papers IEEE PCIC-97-35.
IEEE Std. 1584TM-2002, IEEE Guide for Performing Arc-Flash Hazard Calculations, IEEE Industry Applications Society
Proposal 70E-157a - (Annex XXX), Log #CP8, submitted and accepted by the Technical Committee on Electrical Safety Requirements for Employee Workplaces
TC substantiation statement: “This proposal presents the best information available to date on arc fault hazards. Public review and comments are strongly encouraged. Recent testing has enabled development of improved equations for calculating the arc flash incident energy at the arc flash boundary. While the testing and development of methods is not complete this proposal contains methods that reflect significantly more laboratory data than the existing methods and will allow improved safety.”
Equations:
B-2 Basic Equations for Calculating Incident Energy and Flash Protection Boundary Distances of Equipment.
The following equations can be used to predict the incident energy and flash protection boundary distances produced by a three-phase arc and the flash protection boundary distance for that arc, based on the voltage range. The parameters required to make the calculation are:
(a) The maximum “bolted fault” three-phase short circuit current available at the equipment,
(b) The total protective device clearing time (upstream of the prospective arc location) at the arcing current,
(c) The distance of the worker from the arc for the task to be performed.
Voltage Range: | Calculation: | Equation:
Vo < 1000 Volts | *Ia | lg Ia = K + 0.662 lg Ibf + 0.0966 V + 0.000526 G + 0.5588 V (lg Ibf) – 0.00304 G (lg Ibf)
| Ei | Ei = 416 Ia t D –1.6
| Db | Db = (416 Ia t / 1.2)0.625 | * Ia equation from IEEE 1584-2002 where:
|  |  | lg | is the log10
where: |  |  | Ia | is arcing current (kA)
Vo is the open circuit voltage of the system, |  |  | K | is –0.097 for box conﬁgurations
Ia is the arcing current in kA, |  |  | Ibf | is bolted fault current for three-phase faults (symmetrical RMS) (kA)
Ib is the bolted fault current (from 0.6 to 106 kA), |  |  | V | is system voltage (kV)
Ei is the incident energy in cal/cm 2, |  |  | G | is the gap between conductors, (calculator uses 25mm = 1 inch)
D is the distance of the worker from the arc in inches (18 inches or more),
t is the time of arc exposure in seconds, and
Db is the boundary distance in inches from the arc (distance where incident energy is 1.2 cal/cm 2).
Other Information:
Calculation of Incident Energy Exposure for Open Air Arcs.
The incident energy from open arcs can be better calculated through calculation programs that are commercially available in the marketplace. Most equipment incident energy values would be of the arc-in-box type, since a majority of work on voltages up through 15000 volts is in motor control cabinets, pad-mount switches, and other enclosures.

## Typical Calculations
Typical Flash Protection Boundaries for 3-Phase, 480-volt systems
(Arc-in-Box)
| Clearing | Calculated Flash | Arc Incident Energy
3-Phase Bolted | Time | Protection Boundary (inches) | cal/cm2 at 18 Inches
Fault Current (kA) | (sec) | Arc in a Box | Arc in a Box
50 | 0.05 | 52.3876 | 6.63
| 0.1 | 80.7927 | 13.2599
| 0.2 | 124.5994 | 26.5198
48 | 0.05 | 51.4598 | 6.4431
| 0.1 | 79.3619 | 12.8862
| 0.2 | 122.3928 | 25.7724
46 | 0.05 | 50.489 | 6.2497
46000 | 0.1 | 77.8646 | 12.4994
| 0.2 | 120.0836 | 24.9988
44 | 0.05 | 49.4734 | 6.0498
| 0.1 | 76.2984 | 12.0996
| 0.2 | 117.6682 | 24.1991
42 | 0.05 | 48.4114 | 5.8433
| 0.1 | 74.6605 | 11.6867
| 0.2 | 115.1423 | 23.3734
40 | 0.05 | 47.3009 | 5.6304
| 0.1 | 72.948 | 11.2607
| 0.2 | 112.5012 | 22.5215
38 | 0.05 | 46.1398 | 5.4109
| 0.1 | 71.1573 | 10.8217
| 0.2 | 109.7396 | 21.6434
36 | 0.05 | 44.9255 | 5.1848
| 0.1 | 69.2847 | 10.3697
| 0.2 | 106.8515 | 20.7393
34 | 0.05 | 43.6553 | 4.9523
| 0.1 | 67.3257 | 9.9045
| 0.2 | 103.8304 | 19.8091
32 | 0.05 | 42.3259 | 4.7132
| 0.1 | 65.2754 | 9.4264
| 0.2 | 100.6684 | 18.8527
30 | 0.05 | 40.9335 | 4.4676
| 0.1 | 63.1281 | 8.9351
| 0.2 | 97.3568 | 17.8703
28 | 0.05 | 39.4739 | 4.2154
| 0.1 | 60.8771 | 8.4309
| 0.2 | 93.8853 | 16.8617
26 | 0.05 | 37.9421 | 3.9568
| 0.1 | 58.5147 | 7.9135
| 0.2 | 90.242 | 15.827
24 | 0.05 | 36.3321 | 3.6916
| 0.1 | 56.0317 | 7.3831
| 0.2 | 86.4128 | 14.7662
22 | 0.05 | 34.6368 | 3.4198
| 0.1 | 53.4172 | 6.8397
| 0.2 | 82.3806 | 13.6793
20 | 0.05 | 32.8475 | 3.1416
| 0.1 | 50.6577 | 6.2832
| 0.2 | 78.1249 | 12.5663
18 | 0.05 | 30.9534 | 2.8568
| 0.1 | 47.7367 | 5.7136
| 0.2 | 73.6201 | 11.4272
16 | 0.05 | 28.9411 | 2.5655
| 0.1 | 44.6333 | 5.131
| 0.2 | 68.834 | 10.2619
14 | 0.05 | 26.7929 | 2.2676
| 0.1 | 41.3202 | 4.5353
| 0.2 | 63.7245 | 9.0706
12 | 0.05 | 24.4849 | 1.9633
| 0.1 | 37.7609 | 3.9266
| 0.2 | 58.2353 | 7.8531
10 | 0.05 | 21.9839 | 1.6524
| 0.1 | 33.9038 | 3.3048
| 0.2 | 52.2868 | 6.6096
8 | 0.05 | 19.2399 | 1.335
| 0.1 | 29.672 | 2.6699
| 0.2 | 45.7605 | 5.3399
6 | 0.05 | 16.1718 | 1.011
| 0.1 | 24.9403 | 2.022
| 0.2 | 38.4632 | 4.0441
4 | 0.05 | 12.6275 | 0.68054
| 0.1 | 19.4743 | 1.3611
| 0.2 | 30.0334 | 2.7222