## 25F nomo
Covington-Duwamish (SCL) #1 230kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 016
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6618.55
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -824.81 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 323.36 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | -216.66 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 565.87 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 323.36 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 936.1 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | -577.71 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1503.71 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | -15.72 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1999.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 565.87 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | -216.66 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | -275.97 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | -15.72 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 311.96 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 311.96 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 936.1 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 946.58 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 333.14 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1486.46 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 946.58 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -824.81 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1503.71 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -577.71 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 848.48 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | -275.97 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1486.46 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 333.14 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1999.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 848.48 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Covington-Duwamish (SCL) #1 230kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 016
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6292.734
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -328.64 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 835.69 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 258.83 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1066.48 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 835.69 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1390.38 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | -102.08 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1943.34 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 502.87 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2463.68 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1066.48 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 258.83 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 239.98 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 502.87 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 802.69 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 802.69 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1390.38 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1406.98 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 818.85 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1903.59 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1406.98 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -328.64 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1943.34 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -102.08 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1326.06 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 239.98 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1903.59 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 818.85 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2463.68 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1326.06 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Covington-Duwamish (SCL) #1 230kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 016
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6017.864
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 148.99 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1256.53 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 728.88 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1474.87 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1256.53 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1827.14 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 383.25 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2384.38 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 949.11 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2854.56 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1474.87 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 728.88 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 712.73 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 949.11 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1266.6 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1266.6 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1827.14 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1855.11 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1275.56 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2367.61 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1855.11 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 148.99 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2384.38 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 383.25 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1792.19 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 712.73 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2367.61 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1275.56 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2854.56 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1792.19 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Covington-Duwamish (SCL) #1 230kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 016
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4972.7733
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1971.23 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2825.96 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2541.59 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2920.5 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2825.96 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2854.27 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2207.19 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3310.07 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 460 | 2726.12 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1830.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2920.5 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2541.59 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2478.42 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2726.12 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3068.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3068.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2854.27 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3146.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3047.28 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1896.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3146.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1971.23 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3310.07 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2207.19 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2006.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2478.42 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1896.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3047.28 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1830.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2006.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Covington-Duwamish (SCL) #1 230kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 016
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4635.438
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2470.31 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2450.51 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2676.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2568.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2450.51 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2777.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2533.94 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3077.53 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2545.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1596.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2568.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2676.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2734.27 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2545.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2743.94 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2743.94 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2777.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3059.25 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3037.85 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1695.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3059.25 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2470.31 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3077.53 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2533.94 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 1804.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2734.27 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1695.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3037.85 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1596.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1804.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Covington-Duwamish (SCL) #1 230kV Line(COV-CRES BYP @ COV)
G0 | -824.81 | -328.64 | 148.99 | 1971.23 | 2470.31
G1 | -216.66 | 258.83 | 728.88 | 2541.59 | 2676.32 | Season/Year: | WINTER 2009
G2 | 323.36 | 835.69 | 1256.53 | 2825.96 | 2450.51 | Direction: | South-to-North (SN)
G3 | -577.71 | -102.08 | 383.25 | 2207.19 | 2533.94 | Case Loads: | Heavy Loads
G4 | -15.72 | 502.87 | 949.11 | 2726.12 | 2545.91 | Outage: | 016
G5 | 565.87 | 1066.48 | 1474.87 | 2920.5 | 2568.06 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | -275.97 | 239.98 | 712.73 | 2478.42 | 2734.27 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 311.96 | 802.69 | 1266.6 | 3068.03 | 2743.94 | Study Person: | FRP9899
G8 | 936.1 | 1390.38 | 1827.14 | 2854.27 | 2777.06 | Source: | 016WINTER09v1SNH
G9 | 333.14 | 818.85 | 1275.56 | 3047.28 | 3037.85
G10 | 946.58 | 1406.98 | 1855.11 | 3146.24 | 3059.25
G11 | 1503.71 | 1943.34 | 2384.38 | 3310.07 | 3077.53
G12 | 848.48 | 1326.06 | 1792.19 | 2006.93 | 1804.42
G13 | 1486.46 | 1903.59 | 2367.61 | 1896.81 | 1695.64
G14 | 1999.67 | 2463.68 | 2854.56 | 1830.64 | 1596.55
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | CTG_FAIL_IN_FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 016 | Covington-Duwamish (SCL) #1 230kV Line(COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6618.55 | -824.81 | -216.66 | 323.36 | -577.71 | -15.72 | 565.87 | -275.97 | 311.96 | 936.1 | 333.14 | 946.58 | 1503.71 | 848.48 | 1486.46 | 1999.67
35F | 6292.734 | -328.64 | 258.83 | 835.69 | -102.08 | 502.87 | 1066.48 | 239.98 | 802.69 | 1390.38 | 818.85 | 1406.98 | 1943.34 | 1326.06 | 1903.59 | 2463.68
45F | 6017.864 | 148.99 | 728.88 | 1256.53 | 383.25 | 949.11 | 1474.87 | 712.73 | 1266.6 | 1827.14 | 1275.56 | 1855.11 | 2384.38 | 1792.19 | 2367.61 | 2854.56
60F | 4972.7733 | 1971.23 | 2541.59 | 2825.96 | 2207.19 | 2726.12 | 2920.5 | 2478.42 | 3068.03 | 2854.27 | 3047.28 | 3146.24 | 3310.07 | 2006.93 | 1896.81 | 1830.64
70F | 4635.438 | 2470.31 | 2676.32 | 2450.51 | 2533.94 | 2545.91 | 2568.06 | 2734.27 | 2743.94 | 2777.06 | 3037.85 | 3059.25 | 3077.53 | 1804.42 | 1695.64 | 1596.55

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -826.21 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 522.02 | 521.92 | 6655.6 | -824.81 | 274.24 | FULL
G1 | -218.21 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 522.02 | 522.02 | 6589.08 | -216.66 | -38.37 | FULL
G2 | 321.5 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 521.96 | 521.97 | 6603.82 | 323.36 | -311.52 | FULL
G3 | -579.39 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 522.49 | 522.47 | 6654.04 | -577.71 | 197.8 | FULL
G4 | -17.09 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 522.33 | 522.31 | 6583.91 | -15.72 | -78.84 | FULL
G5 | 564.17 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 522.47 | 522.39 | 6604.17 | 565.87 | -384.32 | FULL
G6 | -277.15 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 522.66 | 522.62 | 6652.77 | -275.97 | 151.33 | FULL
G7 | 310.5 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 522.62 | 522.61 | 6584.5 | 311.96 | -146.31 | FULL
G8 | 936.28 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 523.08 | 523.07 | 6606.34 | 936.1 | -473.47 | FULL
G9 | 331.4 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 522.88 | 522.89 | 6654.58 | 333.14 | 17.39 | FULL
G10 | 945.97 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 523.6 | 523.55 | 6591.69 | 946.58 | -309.9 | FULL
G11 | 1503.81 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 523.08 | 523.12 | 6614.07 | 1503.71 | -592.31 | FULL
G12 | 848.38 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 522.78 | 522.78 | 6660.59 | 848.48 | -122.91 | FULL
G13 | 1486.51 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 522.96 | 522.98 | 6600.07 | 1486.46 | -458.05 | FULL
G14 | 2000.32 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 522.42 | 522.47 | 6623.02 | 1999.67 | -727.97 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -330.87 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 506.87 | 506.8 | 6325.22 | -328.64 | 35.9 | FULL
G1 | 258.61 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 506.59 | 506.56 | 6257.96 | 258.83 | -266.64 | FULL
G2 | 835.16 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 507.32 | 507.33 | 6281.07 | 835.69 | -567.7 | FULL
G3 | -103.38 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 506.94 | 507.05 | 6320.91 | -102.08 | -23.82 | FULL
G4 | 502.38 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 506.93 | 506.88 | 6257.87 | 502.87 | -343.19 | FULL
G5 | 1066.43 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 507.31 | 507.35 | 6282.27 | 1066.48 | -629.03 | FULL
G6 | 238.06 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 507.3 | 507.3 | 6320.4 | 239.98 | -97.12 | FULL
G7 | 803.99 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 507.23 | 507.19 | 6259.26 | 802.69 | -389.38 | FULL
G8 | 1390.44 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 507.32 | 507.35 | 6284.12 | 1390.38 | -695.79 | FULL
G9 | 816.36 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 507.27 | 507.25 | 6327.41 | 818.85 | -221.85 | FULL
G10 | 1404.96 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 507.73 | 507.78 | 6267.61 | 1406.98 | -536.43 | FULL
G11 | 1943.28 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 507.64 | 507.67 | 6291.76 | 1943.34 | -812.77 | FULL
G12 | 1325.89 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 507.25 | 507.2 | 6335.1 | 1326.06 | -358.95 | FULL
G13 | 1903.41 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 507.56 | 507.58 | 6276.32 | 1903.59 | -668.1 | FULL
G14 | 2462.27 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 506.68 | 506.77 | 6303.73 | 2463.68 | -956.86 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 147.77 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.43 | 494.41 | 6041.27 | 148.99 | -213.84 | FULL
G1 | 727.97 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.12 | 494.13 | 5982.49 | 728.88 | -523.47 | FULL
G2 | 1256.21 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 493.9 | 493.94 | 6007.56 | 1256.53 | -794.91 | FULL
G3 | 381.15 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.74 | 494.75 | 6041.21 | 383.25 | -283.62 | FULL
G4 | 950.27 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.35 | 494.37 | 5983 | 949.11 | -585.64 | FULL
G5 | 1474.56 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.12 | 494.19 | 6008.69 | 1474.87 | -855.51 | FULL
G6 | 712.17 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.94 | 494.91 | 6042.78 | 712.73 | -352.69 | FULL
G7 | 1266.15 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.31 | 494.33 | 5984.92 | 1266.6 | -648.02 | FULL
G8 | 1828.9 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.39 | 494.44 | 6011.93 | 1827.14 | -928.79 | FULL
G9 | 1274.52 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.84 | 494.78 | 6050.82 | 1275.56 | -468.83 | FULL
G10 | 1855.23 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.59 | 494.62 | 5993.95 | 1855.11 | -776.46 | FULL
G11 | 2385.31 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.94 | 494.91 | 6021.15 | 2384.38 | -1050.81 | FULL
G12 | 1793.3 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.45 | 494.47 | 6060.19 | 1792.19 | -620.55 | FULL
G13 | 2366.74 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 495.15 | 495.2 | 6004.67 | 2367.61 | -919.02 | FULL
G14 | 2854.83 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 494.18 | 494.12 | 6033.33 | 2854.56 | -1177.84 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1972.09 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 473.44 | 473.51 | 5004.42 | 1971.23 | -1147.03 | FULL
G1 | 2541.87 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 473.18 | 473.07 | 4957.26 | 2541.59 | -1459.93 | FULL
G2 | 2827.19 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2411.59 | -2410.75 | 4978.34 | 2825.96 | -1593.54 | CTG_FAIL_IN_FULL
G3 | 2205.34 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 473.48 | 473.44 | 5006.99 | 2207.19 | -1233.55 | FULL
G4 | 2726.51 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 473.47 | 473.51 | 4959.78 | 2726.12 | -1502.13 | FULL
G5 | 2920.97 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2410.84 | -2410.12 | 4975.95 | 2920.5 | -1585.24 | CTG_FAIL_IN_FULL
G6 | 2478.06 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 474.26 | 474.25 | 5009.98 | 2478.42 | -1270.47 | FULL
G7 | 3068.46 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2391.19 | -2390.46 | 4963.28 | 3068.03 | -1584.13 | CTG_FAIL_IN_FULL
G8 | 2854.74 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2218.1 | -2219.69 | 4968.5 | 2854.27 | -1417.14 | FULL
G9 | 3047.74 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 473.59 | 473.53 | 5022.24 | 3047.28 | -1389.42 | FULL
G10 | 3146.79 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2222.11 | -2221.14 | 4958.21 | 3146.24 | -1420.14 | FULL
G11 | 3310.49 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3281 | 3278.02 | 4971.43 | 3310.07 | -1481.28 | FULL
G12 | 2007.1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -424.05 | -423.94 | 4981.42 | 2006.93 | -628.26 | FULL
G13 | 1898.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -422.76 | -422.66 | 4911.13 | 1896.81 | -532.53 | FULL
G14 | 1830.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -425.39 | -425.33 | 4922.67 | 1830.64 | -461.85 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2470.81 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.91 | 457.75 | 457.65 | 4687.92 | 2470.31 | -1407.47 | FULL
G1 | 2676.69 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2298.04 | -2297.38 | 4623.97 | 2676.32 | -1498.17 | CTG_FAIL_IN_FULL
G2 | 2452.67 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2138.16 | -2136.78 | 4629.18 | 2450.51 | -1346.45 | FULL
G3 | 2534.14 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2146.51 | -2147.4 | 4684.98 | 2533.94 | -1389.35 | FULL
G4 | 2546.21 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2136.31 | -2137.99 | 4616.34 | 2545.91 | -1358.48 | FULL
G5 | 2567.46 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2149.67 | -2150.62 | 4626.58 | 2568.06 | -1345.47 | FULL
G6 | 2735.86 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2148.53 | -2146.52 | 4684.35 | 2734.27 | -1377.69 | FULL
G7 | 2746.41 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2142.77 | -2143.36 | 4614.57 | 2743.94 | -1352.98 | FULL
G8 | 2778.71 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2154.53 | -2152.81 | 4627.53 | 2777.06 | -1342.13 | FULL
G9 | 3039.98 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2140.8 | -2139.2 | 4686.13 | 3037.85 | -1346.8 | FULL
G10 | 3061.44 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2144.25 | -2142.85 | 4616.8 | 3059.25 | -1329.12 | FULL
G11 | 3079.81 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2145.14 | -2143.6 | 4629.5 | 3077.53 | -1309.48 | FULL
G12 | 1804.94 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -424.72 | -424.77 | 4643.23 | 1804.42 | -480.07 | FULL
G13 | 1697.58 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -422.77 | -422.74 | 4573.73 | 1695.64 | -377.98 | FULL
G14 | 1596.21 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -423.2 | -423.16 | 4586.76 | 1596.55 | -295.5 | FULL
016WINTER09v1SNH