## 25F nomo
Snohomish-Bothell (SCL) #1 or #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 042
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6648.3433
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 376.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 595.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 546.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1609.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 595.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3362.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1380.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2907.83 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1490.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2701.91 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1609.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 546.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3134.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1490.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3250.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3250.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3362.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3195.26 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3116.58 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3059.52 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3195.26 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 376.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2907.83 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1380.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2984.79 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3134.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 3059.52 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3116.58 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2701.91 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2984.79 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Snohomish-Bothell (SCL) #1 or #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 042
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6319.518
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 736.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 964.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 855.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1927.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 964.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3358.79 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1692.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3064.98 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1805.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2902.22 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1927.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 855.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3348.14 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1805.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3364.35 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3364.35 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3358.79 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3010.63 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2929.44 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2862.05 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3010.63 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 736.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3064.98 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1692.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2738.61 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3348.14 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2862.05 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2929.44 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2902.22 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2738.61 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Snohomish-Bothell (SCL) #1 or #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 042
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6033.118
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 479.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 700.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 592.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1626.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 700.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3305.36 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1432.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2973.46 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1516.44 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2844.79 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1626.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 592.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3140.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1516.44 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3254.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3254.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3305.36 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2902.84 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2841.41 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2756.98 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2902.84 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 479.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2973.46 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1432.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2532.82 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3140.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2756.98 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2841.41 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2844.79 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2532.82 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Snohomish-Bothell (SCL) #1 or #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 042
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4958.3267
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1834.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2057.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1946.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2865.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2057.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2988.54 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2658.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2540.86 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2762.67 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1935.84 | N-1: Bothell - HrnchTap 230kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2865.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1946.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2856.3 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2762.67 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2932.22 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2932.22 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2988.54 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2505.4 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2394.07 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1737.08 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2505.4 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1834.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2540.86 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2658.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 1497.63 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2856.3 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1737.08 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2394.07 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1935.84 | N-1: Bothell - HrnchTap 230kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1497.63 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Snohomish-Bothell (SCL) #1 or #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 042
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4623.404
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2070.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2275.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2183.07 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 3018.08 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
100 | 775 | 2275.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2729.33 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2883.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2158.78 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2987.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1570.23 | N-1: Bothell - HrnchTap 230kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3018.08 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2183.07 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2695.23 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2987.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2774.87 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2774.87 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2729.33 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2326.47 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2089.44 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1431.15 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2326.47 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2070.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2158.78 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2883.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 1172.34 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2695.23 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1431.15 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2089.44 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1570.23 | N-1: Bothell - HrnchTap 230kV | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1172.34 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Snohomish-Bothell (SCL) #1 or #2 230kV Line (COV-CRES BYP @ COV)
G0 | 376.15 | 736.16 | 479.88 | 1834.61 | 2070.38
G1 | 546.55 | 855.91 | 592.12 | 1946.22 | 2183.07 | Season/Year: | WINTER 2009
G2 | 595.21 | 964.32 | 700.21 | 2057.62 | 2275.86 | Direction: | North-to-South (NS)
G3 | 1380.9 | 1692.8 | 1432.58 | 2658.38 | 2883.94 | Case Loads: | Heavy Loads
G4 | 1490.16 | 1805.93 | 1516.44 | 2762.67 | 2987.34 | Outage: | 042
G5 | 1609.32 | 1927.13 | 1626.86 | 2865.27 | 3018.08 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3134.76 | 3348.14 | 3140.73 | 2856.3 | 2695.23 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3250.29 | 3364.35 | 3254.89 | 2932.22 | 2774.87 | Study Person: | FRP9899
G8 | 3362.21 | 3358.79 | 3305.36 | 2988.54 | 2729.33 | Source: | 042WINTER09v2NSH
G9 | 3116.58 | 2929.44 | 2841.41 | 2394.07 | 2089.44
G10 | 3195.26 | 3010.63 | 2902.84 | 2505.4 | 2326.47
G11 | 2907.83 | 3064.98 | 2973.46 | 2540.86 | 2158.78
G12 | 2984.79 | 2738.61 | 2532.82 | 1497.63 | 1172.34
G13 | 3059.52 | 2862.05 | 2756.98 | 1737.08 | 1431.15
G14 | 2701.91 | 2902.22 | 2844.79 | 1935.84 | 1570.23
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 042 | Snohomish-Bothell (SCL) #1 or #2 230kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6648.3433 | 376.15 | 546.55 | 595.21 | 1380.9 | 1490.16 | 1609.32 | 3134.76 | 3250.29 | 3362.21 | 3116.58 | 3195.26 | 2907.83 | 2984.79 | 3059.52 | 2701.91
35F | 6319.518 | 736.16 | 855.91 | 964.32 | 1692.8 | 1805.93 | 1927.13 | 3348.14 | 3364.35 | 3358.79 | 2929.44 | 3010.63 | 3064.98 | 2738.61 | 2862.05 | 2902.22
45F | 6033.118 | 479.88 | 592.12 | 700.21 | 1432.58 | 1516.44 | 1626.86 | 3140.73 | 3254.89 | 3305.36 | 2841.41 | 2902.84 | 2973.46 | 2532.82 | 2756.98 | 2844.79
60F | 4958.3267 | 1834.61 | 1946.22 | 2057.62 | 2658.38 | 2762.67 | 2865.27 | 2856.3 | 2932.22 | 2988.54 | 2394.07 | 2505.4 | 2540.86 | 1497.63 | 1737.08 | 1935.84
70F | 4623.404 | 2070.38 | 2183.07 | 2275.86 | 2883.94 | 2987.34 | 3018.08 | 2695.23 | 2774.87 | 2729.33 | 2089.44 | 2326.47 | 2158.78 | 1172.34 | 1431.15 | 1570.23

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 375.05 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 473.35 | 473.3 | 6654.72 | 376.15 | 45.4 | FULL
G1 | 545.99 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 476 | 475.94 | 6583.16 | 546.55 | 182.42 | FULL
G2 | 594.56 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 474.09 | 474.01 | 6594.47 | 595.21 | 235.61 | FULL
G3 | 1382.82 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 484.67 | 484.55 | 6650.83 | 1380.9 | 679.39 | FULL
G4 | 1493.11 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 485.15 | 484.98 | 6583.21 | 1490.16 | 772.55 | FULL
G5 | 1611.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 485.72 | 485.58 | 6597.09 | 1609.32 | 872.14 | FULL
G6 | 3150.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 492.35 | 492.24 | 6693.6 | 3134.76 | 1786.56 | FULL
G7 | 3266.16 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 490.89 | 490.77 | 6631.93 | 3250.29 | 1882.15 | FULL
G8 | 3380.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 490.73 | 490.71 | 6651.19 | 3362.21 | 1982.67 | FULL
G9 | 3131.37 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -13.33 | -547.79 | -547.72 | 6716.27 | 3116.58 | 1974.17 | FULL
G10 | 3211.67 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -13.33 | -545.58 | -545.5 | 6654.2 | 3195.26 | 2047.73 | FULL
G11 | 2920.61 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.89 | 457.35 | 457.3 | 6655.25 | 2907.83 | 1937.18 | FULL
G12 | 2999.13 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -13.33 | -545.93 | -545.93 | 6728.02 | 2984.79 | 2051.15 | FULL
G13 | 3074.85 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -13.33 | -546.33 | -546.28 | 6666.56 | 3059.52 | 2123.46 | FULL
G14 | 2713.13 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.89 | 460.02 | 460.06 | 6664.65 | 2701.91 | 1951.99 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 735.65 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 469.38 | 469.24 | 6318.99 | 736.16 | 289.89 | FULL
G1 | 854.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 469.89 | 469.68 | 6249.36 | 855.91 | 391.23 | FULL
G2 | 962.97 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 470.04 | 469.86 | 6262.01 | 964.32 | 485.06 | FULL
G3 | 1697.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 478.39 | 478.29 | 6321.74 | 1692.8 | 892.1 | FULL
G4 | 1811.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 478.7 | 478.85 | 6255.28 | 1805.93 | 988.5 | FULL
G5 | 1932.47 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 479.41 | 479.17 | 6271.33 | 1927.13 | 1093.33 | FULL
G6 | 3366.66 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -13.33 | -533.25 | -533.14 | 6374.58 | 3348.14 | 1936.11 | FULL
G7 | 3383.84 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -13.33 | -535.53 | -535.44 | 6310.87 | 3364.35 | 1986.9 | FULL
G8 | 3378.2 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | -13.22 | -549.78 | -532.73 | 6328.69 | 3358.79 | 2012.88 | FULL
G9 | 2942.91 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -13.33 | -515.05 | -514.73 | 6379.75 | 2929.44 | 1913.41 | FULL
G10 | 3024.46 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -13.33 | -529.39 | -529.29 | 6317.55 | 3010.63 | 1973.63 | FULL
G11 | 3078.72 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -13.33 | -530.18 | -530.1 | 6335.84 | 3064.98 | 2049.25 | FULL
G12 | 2750.03 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -7.45 | -512.03 | -511.99 | 6389.88 | 2738.61 | 1960.23 | FULL
G13 | 2875.04 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -13.33 | -530.55 | -530.5 | 6330.09 | 2862.05 | 2054.08 | FULL
G14 | 2915.06 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -13.33 | -526.92 | -526.76 | 6346.81 | 2902.22 | 2105.86 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 478.93 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 435.16 | 435.06 | 6035.26 | 479.88 | 159.64 | FULL
G1 | 591.56 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 435.41 | 435.31 | 5965.34 | 592.12 | 256.89 | FULL
G2 | 698.07 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 435.62 | 435.46 | 5977.65 | 700.21 | 350.79 | FULL
G3 | 1436.48 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 443.71 | 443.75 | 6036.04 | 1432.58 | 760.57 | FULL
G4 | 1519.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 442.84 | 442.94 | 5968.49 | 1516.44 | 840.84 | FULL
G5 | 1630.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 443.41 | 443.54 | 5983.8 | 1626.86 | 934.85 | FULL
G6 | 3157.12 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 446.68 | 446.75 | 6082.89 | 3140.73 | 1836.42 | FULL
G7 | 3271.6 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 446.56 | 446.59 | 6020.93 | 3254.89 | 1936.83 | FULL
G8 | 3322.43 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -13.33 | -513.66 | -513.4 | 6039.33 | 3305.36 | 2005.86 | FULL
G9 | 2853.68 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -13.33 | -508.34 | -508.32 | 6094.75 | 2841.41 | 1874.52 | FULL
G10 | 2916.3 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -13.33 | -508.68 | -508.53 | 6032.06 | 2902.84 | 1941.49 | FULL
G11 | 2987.22 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -13.33 | -512.79 | -512.71 | 6050.6 | 2973.46 | 2010.21 | FULL
G12 | 2542.11 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -7.45 | -501.02 | -501.06 | 6100.01 | 2532.82 | 1851.41 | FULL
G13 | 2768.56 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -13.33 | -508.73 | -508.72 | 6044.92 | 2756.98 | 2028.59 | FULL
G14 | 2857.49 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -13.33 | -517.05 | -517 | 6064.7 | 2844.79 | 2091.45 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1839.35 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 443.53 | 443.63 | 4963.65 | 1834.61 | 1056.09 | FULL
G1 | 1951.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 443.79 | 443.91 | 4899.53 | 1946.22 | 1150.24 | FULL
G2 | 2064.24 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 444.59 | 444.7 | 4917.12 | 2057.62 | 1243.04 | FULL
G3 | 2670.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 447.93 | 447.9 | 4985.82 | 2658.38 | 1567.9 | FULL
G4 | 2774.4 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 447.8 | 447.95 | 4923.89 | 2762.67 | 1657.16 | FULL
G5 | 2877.69 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 447.74 | 447.78 | 4944.29 | 2865.27 | 1741.14 | FULL
G6 | 2869.18 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -13.33 | -480.92 | -480.62 | 5004.1 | 2856.3 | 1789.1 | FULL
G7 | 2945.31 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -13.33 | -489.42 | -489.38 | 4941.62 | 2932.22 | 1872.46 | FULL
G8 | 3002.39 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -13.33 | -487.16 | -487.1 | 4961.48 | 2988.54 | 1932.35 | FULL
G9 | 2402.37 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -7.45 | -474.58 | -474.54 | 5010.16 | 2394.07 | 1738.23 | FULL
G10 | 2513.55 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -13.33 | -479.27 | -478.93 | 4949.3 | 2505.4 | 1840.13 | FULL
G11 | 2550.46 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -13.33 | -476.29 | -476.17 | 4969.11 | 2540.86 | 1882.49 | FULL
G12 | 1501.57 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -7.45 | -476.67 | -476.52 | 4998.05 | 1497.63 | 1396.24 | FULL
G13 | 1741.32 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -7.45 | -476.55 | -476.53 | 4941.29 | 1737.08 | 1560.2 | FULL
G14 | 1941.07 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | N-1: Bothell - HrnchTap 230kV | -7.6 | -480.73 | -480.71 | 4965.49 | 1935.84 | 1700.7 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2076.28 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 444.52 | 444.6 | 4634.35 | 2070.38 | 1219.6 | FULL
G1 | 2191.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 444.89 | 444.93 | 4571.83 | 2183.07 | 1313.88 | FULL
G2 | 2284.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 444.08 | 444.24 | 4590.39 | 2275.86 | 1393.05 | FULL
G3 | 2895.93 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 447.83 | 447.83 | 4660.75 | 2883.94 | 1721.37 | FULL
G4 | 3001.11 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.56 | 448.13 | 448.11 | 4600.13 | 2987.34 | 1809.57 | FULL
G5 | 3032.02 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.49 | -173.76 | -173.69 | 4619.39 | 3018.08 | 1854.9 | FULL
G6 | 2706.28 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -13.33 | -465.8 | -465.41 | 4665.66 | 2695.23 | 1740.6 | FULL
G7 | 2786.78 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -13.33 | -467.11 | -466.85 | 4604.21 | 2774.87 | 1815.88 | FULL
G8 | 2740.94 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.49 | -173.59 | -173.53 | 4620.73 | 2729.33 | 1820.69 | FULL
G9 | 2096.67 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -7.45 | -462.5 | -462.43 | 4667.47 | 2089.44 | 1600.16 | FULL
G10 | 2335.02 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -7.45 | -462.95 | -462.92 | 4611.5 | 2326.47 | 1762.6 | FULL
G11 | 2166.75 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.49 | -174.2 | -174.19 | 4623.37 | 2158.78 | 1708.69 | FULL
G12 | 1175.2 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -7.45 | -458.44 | -458.38 | 4658.25 | 1172.34 | 1256.56 | FULL
G13 | 1433.07 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -7.45 | -464.7 | -464.8 | 4600.43 | 1431.15 | 1421.03 | FULL
G14 | 1573.7 | Branch BOTHELL (46403) TO SNOH S3 (41329) CKT 1 [230.00 - 230.00 kV] | N-1: Bothell - HrnchTap 230kV | -7.6 | -464.15 | -464.13 | 4622.6 | 1570.23 | 1529.08 | FULL
042WINTER09v2NSH