November 21, 1997

Contract # TW-0928

SPECIAL SPECIFICATION

SECTION 15755-S

HEAT EXCHANGERS

Page

PART 1 - GENERAL

1.01 	Description.	2

1.02	Related Work.	2

1.03	Quality Assurance.	2

1.04	References.	2

1.05	Submittals.	3

1.06 	Delivery, Storage, and Handling.	3

1.07 	Project/Site Conditions.	3

PART 2 - PRODUCTS

2.01	Acceptable Manufacturers.	4

2.02 	Ratings.	4

2.03 	Plate & Frame Heat Exchanger.	5

PART 3 - EXECUTION

3.01 	Inspection.	6

3.02 	Installation/Application/Erection.	6

3.03 	Adjusting and Cleaning.	6

3.04 	Commissioning..	6

3.05 	Demonstration.	7

SPECIAL SPECIFICATION

SECTION 15755-S

HEAT EXCHANGERS

PART 1 - GENERAL

1.01	DESCRIPTION

A.  	This Section includes heat exchangers for mechanical systems.

1.02	RELATED WORK

A.     Section 01300-S

B.  	Section 15010-S

C.  	Section 15250-S

1.03	QUALITY ASSURANCE

A.  	Manufacturer Qualifications:  Firm experienced in manufacturing heat exchangers similar to those indicated for this Project and that have a record of successful in-service performance.

B.  	Fabricate and stamp heat exchangers to comply with American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code, Section VIII, Division 1.

C.  	Provide completely fill-out ASME Form No. U-1 for each heat exchanger to be approved prior to shipping.

1.04	REFERENCES

A.  	ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

B.  	ASME Form No. U-1.

1.05	SUBMITTALS

A.  	Make submittals according to this Section, Section 15010-S, and Section 01300-S.

B.  	Submit a completed ASME Form No. U-1 to be approved prior to shipping.

C. 	Submit product data for each heat exchanger, including rated capacities, pressure drop, weights (shipping, installed, and operating), and installation and startup instructions.

D. 	Submit maintenance data for heat exchangers in the operation and maintenance manual as specified in Section 01300.  Include detailed manufacturer's instructions for servicing heat exchangers.

1.06	DELIVERY, STORAGE, AND HANDLING

A.  	See Section 15010.

1.07	PROJECT/SITE CONDITIONS

A.  	Coordinate layout and installation of heat exchangers with piping system and adjacent work.  Revise locations and elevations to suit field conditions and as approved by the Architect/Engineer (A/E).

PART 2 - PRODUCTS

2.01	ACCEPTABLE  MANUFACTURERS

A.  	Provide products by one of the following:

1.  	Plate Heat Exchangers:

a. 		Alfa-Laval Thermal, Inc.

b. 		Armstrong Pumps, Inc.

c. 		Baltimore Aircoil Company.

ITT Fluid Technology Corporation.; ITT Bell & Gossett.

AGC

B.	Substitutions: only under provisions of Section 1600-S.

2.02	RATINGS

A.  	Plate and Frame

1.  	Process Chilled Water

a. 		Maximum Design Temperature:

1) 	Cold side:  230 deg. F.

2)  	Chilled side:  230 deg. F.

b. 		Maximum Test Pressure:

1)  	Cold side:  225 psi (1551 kPa).

2)  	Chilled side:  225 psi (1551 kPa).

c. 		Maximum Design Pressure:

1)  	Cold side:  150 psi (1034 kPa).

2)  	Chilled side:  150 psi (1034 kPa).

d. 		See Drawing Schedule for additional information.

2.03	PLATE  & FRAME HEAT EXCHANGER

A.  	Construction

1.  	Plate Material:  ASTM A 167, Type 304 stainless-steel shell.

2. 	End Plate Material:  Painted carbon steel.

3.  	Gasket Material:  Nitrile rubber.

4. 	Piping Connections:  Threaded, 2 in. and smaller.

5.  	Piping Connections:  Studded for ANSI flange connection, 4 in. and larger.

6.	Capable of at least 50% extension capacity.

PART 3 - EXECUTION

3.01	INSPECTION

A.  	Inspect elements and surfaces to receive work for compliance with installation tolerances and for structural rigidity, strength, anchors, and other conditions affecting performance of the heat exchanger.  Do not proceed with installation until unsatisfactory conditions have been corrected.

3.02	INSTALLATION/APPLICATION/ERECTION

A.  	Install heat exchangers according to manufacturer's written instructions.

B. 	Install heat exchangers plumb and level; anchor with supports.

C.  	Maintain manufacturer's recommended clearances for service and maintenance.  Install piping connections maintaining clearances for service and maintenance of heat exchangers.

D.  	Install threaded or flanged connections at heat exchangers.

E. 	Install shutoff valves at heat exchanger inlet and outlet connections.

F. 	Insulate as indicated on the Drawings.

3.03	ADJUSTING AND CLEANING

A. 	Inspect exposed finish after completing system installation, including pipe connections, fittings, valves, and specialties.  Remove burrs, dirt, and construction debris, and repair damaged finishes, including chips, scratches, and abrasions.

3.04	COMMISSIONING

A.  	Provide labor, material, equipment, etc., required to facilitate the commissioning process.

B. 	Perform  tests and verification procedures required by the commissioning process when requested by SNL’s Commissioning Authority and directed by the General Contractor’s Test Engineer.

3.05	DEMONSTRATION

A.  Provide the services of a factory-authorized service representative to start-up equipment, demonstrate operation, and train personnel.

END OF SECTION