## 25F nomo
Covington-Columbia #3 230kV Line O/S
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 199
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6550.438
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 454.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 665.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 567.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1681.4 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 665.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3402.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1419.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3006.67 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
260 | 460 | 1572.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 3099.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1681.4 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 567.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3177.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1572.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3224.44 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3224.44 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
525 | 775 | 3402.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2058.21 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1000 | 140 | 3214.13 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3076.69 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2058.21 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 454.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3006.67 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1419.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 3072.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3177.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 3076.69 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3214.13 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3099.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 3072.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Covington-Columbia #3 230kV Line O/S
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 199
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6419.0447
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 673.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 835.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 731.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1796.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 835.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3473.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1562.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3163.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1682.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 3028.32 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1796.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 731.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3281.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1682.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3386.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3386.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3473.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3159 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3140.45 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3021.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3159 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 673.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3163.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1562.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 3003.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3281.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 3021.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3140.45 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3028.32 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 3003.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Covington-Columbia #3 230kV Line O/S
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 199
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 5979.21
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 542.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 763.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 659.44 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1667.46 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 763.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3355.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1473.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3089.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1555.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2944.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1667.46 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 659.44 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3151.65 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1555.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3232.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3232.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3355.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3076.23 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3069.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2933.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3076.23 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 542.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3089.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1473.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2930.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3151.65 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2933.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3069.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2944.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2930.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Covington-Columbia #3 230kV Line O/S
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 199
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4949.676
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1842.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2056.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1973.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2870.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2056.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3303.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2665.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2893.31 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2762.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2748.36 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2870.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1973.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3280.58 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2762.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3288.98 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3288.98 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3303.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2877.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2868.22 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2732.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2877.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1842.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2893.31 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2665.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2717.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3280.58 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2732.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2868.22 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2748.36 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2717.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Covington-Columbia #3 230kV Line O/S
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 199
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4630.746
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2118.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2302.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2206.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 3128.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2302.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3228.31 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2917.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2815.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3010.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2666.54 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3128.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2206.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3204.81 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3010.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3215.67 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3215.67 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3228.31 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2796.4 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2793.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2653.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2796.4 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2118.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2815.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2917.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2598.71 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3204.81 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2653.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2793.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2666.54 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2598.71 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Covington-Columbia #3 230kV Line O/S
G0 | 454.34 | 673.75 | 542.85 | 1842.27 | 2118.23
G1 | 567.23 | 731.93 | 659.44 | 1973.28 | 2206.03 | Season/Year: | WINTER 2009
G2 | 665.08 | 835.05 | 763.92 | 2056.78 | 2302.36 | Direction: | North-to-South (NS)
G3 | 1419.7 | 1562.42 | 1473.06 | 2665.62 | 2917.77 | Case Loads: | Heavy Loads
G4 | 1572.14 | 1682.3 | 1555.88 | 2762.79 | 3010.38 | Outage: | 199
G5 | 1681.4 | 1796.73 | 1667.46 | 2870.77 | 3128.7 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3177.58 | 3281.83 | 3151.65 | 3280.58 | 3204.81 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3224.44 | 3386.94 | 3232.82 | 3288.98 | 3215.67 | Study Person: | FRP9899
G8 | 3402.79 | 3473.8 | 3355.56 | 3303.35 | 3228.31 | Source: | 199WINTER09v5NSH
G9 | 3214.13 | 3140.45 | 3069.73 | 2868.22 | 2793.25
G10 | 2058.21 | 3159 | 3076.23 | 2877.06 | 2796.4
G11 | 3006.67 | 3163.73 | 3089.73 | 2893.31 | 2815.97
G12 | 3072.97 | 3003.73 | 2930.6 | 2717.92 | 2598.71
G13 | 3076.69 | 3021.43 | 2933.71 | 2732.6 | 2653.77
G14 | 3099.56 | 3028.32 | 2944.43 | 2748.36 | 2666.54
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 199 | Covington-Columbia #3 230kV Line O/S
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6550.438 | 454.34 | 567.23 | 665.08 | 1419.7 | 1572.14 | 1681.4 | 3177.58 | 3224.44 | 3402.79 | 3214.13 | 2058.21 | 3006.67 | 3072.97 | 3076.69 | 3099.56
35F | 6419.0447 | 673.75 | 731.93 | 835.05 | 1562.42 | 1682.3 | 1796.73 | 3281.83 | 3386.94 | 3473.8 | 3140.45 | 3159 | 3163.73 | 3003.73 | 3021.43 | 3028.32
45F | 5979.21 | 542.85 | 659.44 | 763.92 | 1473.06 | 1555.88 | 1667.46 | 3151.65 | 3232.82 | 3355.56 | 3069.73 | 3076.23 | 3089.73 | 2930.6 | 2933.71 | 2944.43
60F | 4949.676 | 1842.27 | 1973.28 | 2056.78 | 2665.62 | 2762.79 | 2870.77 | 3280.58 | 3288.98 | 3303.35 | 2868.22 | 2877.06 | 2893.31 | 2717.92 | 2732.6 | 2748.36
70F | 4630.746 | 2118.23 | 2206.03 | 2302.36 | 2917.77 | 3010.38 | 3128.7 | 3204.81 | 3215.67 | 3228.31 | 2793.25 | 2796.4 | 2815.97 | 2598.71 | 2653.77 | 2666.54

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 453.53 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 475.28 | 475.21 | 6556.31 | 454.34 | 45.33 | FULL
G1 | 569 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 475.15 | 475 | 6485.09 | 567.23 | 140.34 | FULL
G2 | 664.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 475.43 | 475.35 | 6496.54 | 665.08 | 226.18 | FULL
G3 | 1421.7 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 484.88 | 484.8 | 6552.51 | 1419.7 | 653.45 | FULL
G4 | 1576.43 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 486.64 | 486.48 | 6484.78 | 1572.14 | 774.2 | FULL
G5 | 1686.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 487.08 | 486.89 | 6498.75 | 1681.4 | 864.22 | FULL
G6 | 3193.46 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 490.29 | 490.15 | 6596.39 | 3177.58 | 1722.35 | FULL
G7 | 3242.11 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 31.56 | 1289.69 | 1302.31 | 6532.47 | 3224.44 | 1789.86 | CTG_FAIL_IN_FULL
G8 | 3421.49 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 490.25 | 490.22 | 6552.52 | 3402.79 | 1926.08 | FULL
G9 | 3231.17 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -510.07 | -509.4 | 6621.46 | 3214.13 | 1948.39 | FULL
G10 | 2068.47 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 31.56 | 938.74 | 1379.43 | 6529.94 | 2058.21 | 1340.18 | CTG_FAIL_IN_FULL
G11 | 3022.62 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 31.55 | 1225.64 | 1237.21 | 6566.51 | 3006.67 | 1887.47 | FULL
G12 | 3087.12 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -511.72 | -511.12 | 6633.02 | 3072.97 | 2018.28 | FULL
G13 | 3091.83 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -512.08 | -511.5 | 6566.85 | 3076.69 | 2048.68 | FULL
G14 | 3115.13 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -515.03 | -514.54 | 6583.43 | 3099.56 | 2095.94 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 673.43 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 470.48 | 470.27 | 6419.09 | 673.75 | 205.85 | FULL
G1 | 731.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 469.31 | 469.09 | 6349.16 | 731.93 | 259.93 | FULL
G2 | 835.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 469.32 | 469.27 | 6361.15 | 835.05 | 348.21 | FULL
G3 | 1564.8 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 477.29 | 477.52 | 6418.71 | 1562.42 | 758.85 | FULL
G4 | 1685.71 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 477.96 | 477.94 | 6351.51 | 1682.3 | 856.15 | FULL
G5 | 1801.56 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 478.6 | 478.6 | 6366.6 | 1796.73 | 949.83 | FULL
G6 | 3298.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 480.9 | 480.85 | 6466.86 | 3281.83 | 1828.93 | FULL
G7 | 3405.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 480.37 | 480.12 | 6404.89 | 3386.94 | 1902.59 | FULL
G8 | 3493.11 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 479.7 | 479.76 | 6424.58 | 3473.8 | 1989.78 | FULL
G9 | 3155.91 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -499.12 | -498.46 | 6485.85 | 3140.45 | 1933.75 | FULL
G10 | 3176.27 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -501.49 | -500.81 | 6420.08 | 3159 | 1980.53 | FULL
G11 | 3180.2 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -499.13 | -498.51 | 6436.39 | 3163.73 | 2004.73 | FULL
G12 | 3018.27 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -500.72 | -500.42 | 6498.19 | 3003.73 | 2006.2 | FULL
G13 | 3035.06 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -502.96 | -502.7 | 6432.86 | 3021.43 | 2057.7 | FULL
G14 | 3042.68 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -501.25 | -500.98 | 6449.75 | 3028.32 | 2078.08 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 541.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 436.58 | 436.48 | 5978.87 | 542.85 | 148.31 | FULL
G1 | 659.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 437.59 | 437.46 | 5908.91 | 659.44 | 245.03 | FULL
G2 | 765.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 437.72 | 437.61 | 5921.2 | 763.92 | 334.14 | FULL
G3 | 1475.44 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 444.74 | 442.6 | 5979.52 | 1473.06 | 733.97 | FULL
G4 | 1557.99 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.84 | 443.05 | 5911.74 | 1555.88 | 810.84 | FULL
G5 | 1670.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 443.51 | 443.7 | 5927.07 | 1667.46 | 902.67 | FULL
G6 | 3166.53 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 445.9 | 445.84 | 6025.27 | 3151.65 | 1755.78 | FULL
G7 | 3249.28 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 445.29 | 445.07 | 5962.74 | 3232.82 | 1829.23 | FULL
G8 | 3374.38 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 445.44 | 445.25 | 5982.91 | 3355.56 | 1946.11 | FULL
G9 | 3084.82 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -491.26 | -490.89 | 6045.97 | 3069.73 | 1920.01 | FULL
G10 | 3091.3 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -491.65 | -491.26 | 5981.01 | 3076.23 | 1940.83 | FULL
G11 | 3104.97 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -492.32 | -491.94 | 5997.52 | 3089.73 | 1976.4 | FULL
G12 | 2943.86 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -493.53 | -492.87 | 6059.15 | 2930.6 | 2002.7 | FULL
G13 | 2946.81 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -492.43 | -491.92 | 5994.52 | 2933.71 | 2009.32 | FULL
G14 | 2958.1 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -491.92 | -491.36 | 6011.75 | 2944.43 | 2044.06 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1847.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 444.13 | 444.24 | 4940.93 | 1842.27 | 994.41 | FULL
G1 | 1979.21 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 444.73 | 445.11 | 4877.22 | 1973.28 | 1095.38 | FULL
G2 | 2063.07 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 444.57 | 444.68 | 4893.98 | 2056.78 | 1171.04 | FULL
G3 | 2677.78 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 447.65 | 447.66 | 4962.79 | 2665.62 | 1495.84 | FULL
G4 | 2774.11 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 447.72 | 447.79 | 4900.11 | 2762.79 | 1578.44 | FULL
G5 | 2883.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 447.78 | 448.29 | 4920.51 | 2870.77 | 1663.82 | FULL
G6 | 3298.08 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -469.62 | -470.21 | 4998.07 | 3280.58 | 1940.58 | FULL
G7 | 3306.55 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -469.06 | -469.61 | 4934.37 | 3288.98 | 1976.83 | FULL
G8 | 3321.47 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -469.67 | -469.18 | 4952.14 | 3303.35 | 2010.71 | FULL
G9 | 2880.96 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -476.5 | -475.74 | 5005.93 | 2868.22 | 1905.89 | FULL
G10 | 2889.78 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -476.14 | -475.39 | 4942.07 | 2877.06 | 1939.41 | FULL
G11 | 2907.4 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -475.88 | -475.15 | 4960.26 | 2893.31 | 1998.33 | FULL
G12 | 2729.12 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -474.89 | -474.2 | 5021.48 | 2717.92 | 1972.13 | FULL
G13 | 2744.36 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -476.73 | -476.08 | 4958.37 | 2732.6 | 2007.74 | FULL
G14 | 2760.37 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -477.54 | -476.89 | 4976.91 | 2748.36 | 2045.77 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2124.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 445.69 | 445.74 | 4624.4 | 2118.23 | 1165.56 | FULL
G1 | 2213.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 444.95 | 445.1 | 4560.67 | 2206.03 | 1244.09 | FULL
G2 | 2310.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 445.01 | 445.13 | 4579.59 | 2302.36 | 1326.4 | FULL
G3 | 2930.73 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 447.96 | 448.05 | 4649.89 | 2917.77 | 1672.15 | FULL
G4 | 3024.22 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 447.9 | 447.98 | 4588.52 | 3010.38 | 1751.11 | FULL
G5 | 3143.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 448.27 | 448.26 | 4611.21 | 3128.7 | 1841.95 | FULL
G6 | 3221.22 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -458.31 | -458.09 | 4675.09 | 3204.81 | 1932.37 | FULL
G7 | 3232.22 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -460.22 | -459.32 | 4611.45 | 3215.67 | 1970.05 | FULL
G8 | 3244.74 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -458.24 | -458.15 | 4630.17 | 3228.31 | 2002.81 | FULL
G9 | 2805.16 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -461.82 | -460.79 | 4682.87 | 2793.25 | 1907.04 | FULL
G10 | 2808.52 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -462.82 | -462.1 | 4618.96 | 2796.4 | 1939.04 | FULL
G11 | 2827.63 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -460.41 | -459.72 | 4638.52 | 2815.97 | 1987.09 | FULL
G12 | 2608.63 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -12.84 | -445.35 | -445.67 | 4697.41 | 2598.71 | 1949.82 | FULL
G13 | 2664.15 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -461.53 | -460.93 | 4636.36 | 2653.77 | 2009.48 | FULL
G14 | 2677.44 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -462 | -461.35 | 4656.08 | 2666.54 | 2030.77 | FULL
199WINTER09v5NSH