*** DRAFT ***

Date: 		4/26/99
Rev Date: 	7/13/99

Project: 	BTev General Support
Doc. No: 	Hance-H990426B

Subject: 	Standards for Cables Used in the BTeV Project

Conductor sizes, overcurrent protection and insulation rating shall be chosen in accordance with the document "Electrical Design Standards for Electronics to be Used in Experiment Apparatus at Fermilab".  That document and the most recent version of this document is available on the BTeV web site.

Cable types must be chosen with regard to fire safety (flame propagation and smoke characteristics).  Cable must be rated to a recognized standard that shows they are self-extinguishing and will not spread a fire.  Cables with low smoke density, toxicity, and corrosivity of gasses are preferred.  Smoke produced by overheated halogenated cable insulation is corrosive to electronics and fatal to the exposed components of the silicon detector.  Whenever possible, cable should be specified as halogen free.

The following information was gleaned from the National Electrical Code Article 725 and other sources.  Check the most recent version of this document.  New types will be added as they are identified and evaluated.  The Electronics Certification Board (ECB) may grant exceptions on a case-by-case basis.  When choosing a cable for an application listed in the "Application" column, try to choose one of the NEC cable types or permitted substitutions; or UL, IEC, or CSA Fire rating from the same row.

Table of Cable Types and Substitutions

| Application | Description | NEC Cable Types | Permitted Substitution | UL Fire Rating* | IEC Fire Rating* | CSA Fire Rating* |
| --- | --- | --- | --- | --- | --- | --- |
| Air ducts | Plenum | CL2P | CMP, CL3P | UL 910 (smoke and flame) | N/a | FT6 |
| Vertical shafts | Riser | CL2R | CMP, CL3P, CL2P, CMR, CL3R | UL 1666 (Vertical riser) | N/a |  |
| Areas other than risers or plenums | General Purpose | CL2 | CMP, CL3P, CL2P, CMR, CL3R, CL2R, CMG, CM, PLTC, CL3, TC | UL 1581 IEEE 383 (Vertical tray) | IEC 332-3 | FT4 |
| Enclosed in conduit, up to 10 feet exposed | General Purpose - Limited Use | CL2X | CMP, CL3P, CL2P, CMR, CL3R, CL2R, CMG, CM, PLTC, CL3, CL2, CMX, CL3X, TC | UL 1581 VW-1 | IEC 332-1 |  |

* Note, The IEC and CSA Fire ratings are not necessarily represented here as equivalent to the UL Fire Ratings.  The UL (US) standards are more comprehensive and stringent than their international counterparts with regard to flammability.  However, the international ratings may be substituted as shown.  The international ratings do imply additional safety and materials requirements.