CONSTRUCTION SPECIFICATION

405.  WIRING

1.	SCOPE

The work shall consist of furnishing, installing, and testing a complete electrical system as specified herein.

2.	DRAWINGS

The drawings are not intended to shoo in full detail all features of the work.  The contractor shall take all measurements and do all cutting on the job site.  The locations of conduit, boxes, switches, fixtures, control panels, and electrical outlets are approximate only and the exact locations shall be checked to determine that they clear all openings, structural members, pipes, and other fixed equipment.

3.	MATERIALS

The Contractor shall submit a complete list of material, fixtures, and equipment to be used which shall show the catalog numbers, cuts, diagrams, and technical ratings.  Each type of material shall be of the same make and quality throughout the entire job.

4.	RIGID CONDUIT

Rigid steel conduit shall be hot-dipped galvanized.  All conduit embedded in concrete shall have a minimum of two (2) inches of concrete covered on all sides when the concrete is exposed to the air and three (3) inches of concrete cover when adjacent to the earth.  Electric Metallic Tubing (EMT-thin-wall) shall not be used.

5.	FLEXIBLE CABLE MOTOR CONNECTIONS

The motors shall be connected with lead covered, galvanized spiral armored cable.  An anti-short bushing shall be used in each spiral, armored cable termination.  All bends shall be so made that the armor will not be injured and the radius of the curve of the inner edge of any bend shall be not less than five (5) times the outside diameter.  The motors of the armored cable connections shall have a bonding strip, extra conductor, or a jumper for grounding continuity.

6.	FLEXIBLE CONDUIT

Flexible conduit connections shall be watertight flexible couplings, Crouse-Hinds Series ECH or equal.  For couplings over 2 feet long, they shall be rigidly supported.

7.	CONDUIT INSTALLATION

All conduit shall be installed in accordance with Article 346 of the National Electrical Code.  All exposed conduit shall be parallel to or perpendicular to the beams.  Where changes in direction of run require a box or fitting, they shall be cast, threaded hubs with gaskets and malleable or cast cover.

8.	CONDUIT SUPPORTS

Conduit shall be supported on approved type of galvanized wall brackets, ceiling trapezes, and concrete expanding metal inserts, and secured by means of metal lag screws with lock washers.  Threaded studs driven in by p power charge and provided with lock washers and nuts are acceptable.  Wooden plugs and fibrous, plastic, or lead inserts are not acceptable.  ‘All clamps and straps shall fit the conduit snugly.

9.	BUSHINGS AND LOCKNUTS

Conduit shall be securely fastened to all enclosures.  Each outside locknut shall be firmly tightened against each inside bushing or locknut for electrical continuity.  Where grounding is necessary, grounding wedges or solderless ground clamps shall be used.

10.	JUNCTION, OUTLET, AND PULL BOXES

All boxes and fittings shall be cast and watertight with threaded hubs, gaskets, and malleable or cast covers.  The number of wires in a box shall be in accordance with NEC, section No. 370-6.

11.	RECEPTACLE OUTLETS

The receptacles shall be 15 amp, 125 volt, heavy duty, grounded and of the standard type capable of receiving two-wire parallel bladed plugs or three-wire plugs having two parallel blades and one ground prong.

12.	WIRE

All wire shall be 600 volt; code grade copper marked in accordance with NEC.  All wire in conduit for receptacles, lighting, and controls shall be Type RHW.  Wire No. 10 AWG and smaller, except control cable shall be solid.  Wire No. 8 AWG and larger shall be stranded.  Wires shall not be pulled into conduit until construction has advance to a point where wires will not be damaged after they have been installed.

13.	GROUNDING

All equipment, including pumps, motors; cabinets, intake and discharge piping, and structural steel framework shall be grounded in accordance with NEC.

Grounding wire shall have a minimum earth cover of 18 inches and 2 inches cover when embedded in concrete.

Connectors and lugs shall be copper alloy of the bolted type for above ground connections.  All connections made in the earth or concrete shall be properly thermo-welded, Caldwelded, SIL FOS method, or brazed.  All connections must be electrically and mechanically sound

Ground rods shall be made of copper, copper clad steel, or hot-dip galvanized stiff carbon steel not less than 3/4 inch diameter and 8 feet long, and driven full length into the earth without being bent or damaged.

14.	WIRE CONNECTORS AND LUGS

Pigtail connections of No. 8 AWG wire and smaller shall be made with Scotchlock or equal, and insulator or copper splice cap and insulator.  All splice caps shall be indented with the proper size pressure tool.  Preinsulated connectors of porcelain or bakelite jacket types (wire-nuts), with, or without metal inserts shall not be used.  All other connectors and lugs shall be solderless, copper or copper alloy, bolted, crimp, or indenter types.  All connections must be electrically and mechanically sound.

15.	CIRCUITS

The Contractor shall furnish a complete set of correctly sized circuit breakers with combined delayed overload protection and fast acting current limiting actin for short circuits.  Circuit breakers shall be sized for motor starting and running protection.

16.	SERVICE ENTRANCE

A meter base connected to a ground rock shall be installed as specified by the electric power supplier.  The service drop shall meet all code requirements and shall be accomplished with suitable equipment for exterior work.

17.	WIRING DIAGRAM

A complete as-built wiring circuit drawing(s) with all points identified shall be furnished in permanent plastic permanently affixed to the inside of the control cabinet door.  All terminals and wires in the control cabinet shall be labeled or tagged as shown on the wiring diagram, a permanent black image on a dimensional, stable base film.

18.	TESTS

Upon completion of the electrical and control system installation, the equipment and controls shall be tested to demonstrate that the requirements of these specifications have been met.  The Contractor shall furnish all instruments and personnel required of the tests.  Tests shall be performed in the presence of the Contracting Officer or his authorized representative.

19.	INSPECTIONS

The Contractor shall be responsible for and meet all requirements for the wiring inspections required by all applicable federal, state and municipal laws, codes, and regulations and shall correct such deficiencies and defects noted in the inspection(s).

20.	PAYMENT

Payment for furnishing and installing the wiring shall be made at the contract lump sum price.  Such payment shall constitute full compensation for all labor, materials, equipment, and all other items necessary and incidental to the completion of the work.