## Input Output sheet
LWST Baseline (2002) Turbine Calculations - Class 4
10 m windspeed | 5.8 | m/s |  | P/Prated | Efficiency
Weibull K parameter | 2 |  |  | 1e-05 | 0%
Rated power | 1500 | kW |  | 0.05 | 54.5%
Rotor Dia. | 70 | meters |  | 0.1 | 74.5%
Hub height | 65 | meters |  | 0.15 | 81.17%
Altitude | 0 | meters |  | 0.2 | 84.5%
Air Density | 1.2249 | kg/m^3 |  | 0.25 | 86.5%
Rotor Cp | 0.47 |  |  | 0.3 | 87.83%
Cut-in windspeed | 3 | m/s |  | 0.35 | 88.79%
Cut-out windspeed | 26 | m/s |  | 0.4 | 89.5%
Power law shear exponent | 0.143 |  |  | 0.45 | 90.06%
Hub height windspeed | 7.5801 |  |  | 0.5 | 90.5%
Rated windspeed | 11.3544 | m/s |  | 0.55 | 90.86%
Conversion Efficiency | 0.95 | 0.015 |  | 0.6 | 91.17%
| 0.005 | 0.005 |  | 0.65 | 91.42%
Soiling Losses | 3.5% |  |  | 0.7 | 91.64%
Array Losses | 5% |  |  | 0.75 | 91.83%
Availability | 98% |  |  | 0.8 | 92%
| Turbine | Weibul Cp | Weibul betz | 0.85 | 92.15%
Energy capture (MWh/year) | 4439.5258 | 7668.5782 | 10177.6991 | 0.9 | 92.28%
Capacity Factor | 33.79% |  |  | 0.95 | 92.39%
Energy capture ratio | 57.89% |  |  | 1 | 92.5%

## Calculation sheet
Wind | Rayleigh Probability | Weibull Probability | Weibull Betz | Weibull Cp | Turbine Energy | Hub power | Efficiency | Turbine power
0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0
0.25 | 0.0068287 | 0.0068287 | 0.00014903 | 0.00011229 | 0 | 0 | #DIV/0! | 0
0.5 | 0.013622 | 0.013622 | 0.0023784 | 0.0017921 | 0 | 0 | #DIV/0! | 0
0.75 | 0.020347 | 0.020347 | 0.011989 | 0.0090336 | 0 | 0 | #DIV/0! | 0
1 | 0.026967 | 0.026967 | 0.037666 | 0.02838 | 0 | 0 | #DIV/0! | 0
1.25 | 0.033451 | 0.033451 | 0.091255 | 0.068758 | 0 | 0 | #DIV/0! | 0
1.5 | 0.039765 | 0.039765 | 0.18746 | 0.14124 | 0 | 0 | #DIV/0! | 0
1.75 | 0.045881 | 0.045881 | 0.34345 | 0.25878 | 0 | 0 | #DIV/0! | 0
2 | 0.051767 | 0.051767 | 0.57845 | 0.43584 | 0 | 0 | #DIV/0! | 0
2.25 | 0.057398 | 0.057398 | 0.9132 | 0.68807 | 0 | 0 | #DIV/0! | 0
2.5 | 0.062749 | 0.062749 | 1.3695 | 1.0318 | 0 | 0 | #DIV/0! | 0
2.75 | 0.067797 | 0.067797 | 1.9694 | 1.4839 | 0 | 0 | #DIV/0! | 0
3 | 0.072521 | 0.072521 | 2.7349 | 2.0607 | 0 | 0 | #DIV/0! | 0
3.25 | 0.076904 | 0.076904 | 3.6874 | 2.7783 | 0.26953 | 38.0287 | 9.216% | 3.5047
3.5 | 0.080931 | 0.080931 | 4.8467 | 3.6518 | 1.0078 | 47.497 | 26.22% | 12.4522
3.75 | 0.08459 | 0.08459 | 6.2307 | 4.6946 | 1.9264 | 58.4192 | 38.98% | 22.7737
4 | 0.087871 | 0.087871 | 7.855 | 5.9185 | 3.0375 | 70.8993 | 48.76% | 34.5674
4.25 | 0.090768 | 0.090768 | 9.7324 | 7.3331 | 4.3506 | 85.0411 | 56.36% | 47.9314
4.5 | 0.093276 | 0.093276 | 11.8721 | 8.9453 | 5.873 | 100.9484 | 62.37% | 62.9638
4.75 | 0.095395 | 0.095395 | 14.2799 | 10.7595 | 7.6089 | 118.7252 | 67.18% | 79.7629
5 | 0.097125 | 0.097125 | 16.9574 | 12.7769 | 9.5597 | 138.4752 | 71.08% | 98.4266
5.25 | 0.098471 | 0.098471 | 19.9024 | 14.9958 | 11.7233 | 160.3023 | 74.27% | 119.0533
5.5 | 0.099439 | 0.099439 | 23.1081 | 17.4113 | 14.0946 | 184.3105 | 76.9% | 141.741
5.75 | 0.10004 | 0.10004 | 26.5637 | 20.015 | 16.6651 | 210.6035 | 79.1% | 166.5878
6 | 0.10028 | 0.10028 | 30.2541 | 22.7955 | 19.4233 | 239.2851 | 80.95% | 193.692
6.25 | 0.10017 | 0.10017 | 34.1601 | 25.7386 | 22.3542 | 270.4594 | 82.51% | 223.1517
6.5 | 0.09974 | 0.09974 | 38.2587 | 28.8268 | 25.4402 | 304.23 | 83.84% | 255.0649
6.75 | 0.098991 | 0.098991 | 42.5234 | 32.04 | 28.6609 | 340.7009 | 84.98% | 289.5299
7 | 0.097945 | 0.097945 | 46.9244 | 35.356 | 31.9933 | 379.9759 | 85.96% | 326.6448
7.25 | 0.096622 | 0.096622 | 51.4292 | 38.7503 | 35.4127 | 422.1589 | 86.82% | 366.5078
7.5 | 0.09504 | 0.09504 | 56.0031 | 42.1966 | 38.8921 | 467.3538 | 87.56% | 409.2169
7.75 | 0.093221 | 0.093221 | 60.6096 | 45.6674 | 42.4037 | 515.6643 | 88.21% | 454.8703
8 | 0.091186 | 0.091186 | 65.2108 | 49.1343 | 45.9183 | 567.1944 | 88.78% | 503.5663
8.25 | 0.088956 | 0.088956 | 69.7684 | 52.5683 | 49.4066 | 622.0479 | 89.29% | 555.4028
8.5 | 0.086553 | 0.086553 | 74.2438 | 55.9404 | 52.8388 | 680.3286 | 89.73% | 610.4781
8.75 | 0.083998 | 0.083998 | 78.5988 | 59.2217 | 56.1857 | 742.1405 | 90.13% | 668.8903
9 | 0.081314 | 0.081314 | 82.7962 | 62.3844 | 59.4188 | 807.5873 | 90.48% | 730.7376
9.25 | 0.078519 | 0.078519 | 86.8006 | 65.4015 | 62.5107 | 876.773 | 90.8% | 796.118
9.5 | 0.075637 | 0.075637 | 90.5781 | 68.2477 | 65.4355 | 949.8013 | 91.09% | 865.1298
9.75 | 0.072685 | 0.072685 | 94.0975 | 70.8995 | 68.169 | 1026.7762 | 91.34% | 937.8711
10 | 0.069683 | 0.069683 | 97.3304 | 73.3354 | 70.6894 | 1107.8015 | 91.57% | 1014.44
10.25 | 0.06665 | 0.06665 | 100.2515 | 75.5364 | 72.9772 | 1192.9811 | 91.78% | 1094.9347
10.5 | 0.063602 | 0.063602 | 102.8389 | 77.4859 | 75.0153 | 1282.4187 | 91.97% | 1179.4533
10.75 | 0.060555 | 0.060555 | 105.0744 | 79.1702 | 76.7896 | 1376.2184 | 92.14% | 1268.0939
11 | 0.057525 | 0.057525 | 106.9435 | 80.5786 | 78.2888 | 1474.4838 | 92.3% | 1360.9548
11.25 | 0.054525 | 0.054525 | 108.4357 | 81.7029 | 79.5045 | 1577.319 | 92.44% | 1458.134
11.5 | 0.051568 | 0.051568 | 109.5444 | 82.5383 | 77.3513 | 1621.6216 | 92.5% | 1500
11.75 | 0.048664 | 0.048664 | 110.2668 | 83.0826 | 72.9965 | 1621.6216 | 92.5% | 1500
12 | 0.045825 | 0.045825 | 110.604 | 83.3366 | 68.7382 | 1621.6216 | 92.5% | 1500
12.25 | 0.04306 | 0.04306 | 110.5606 | 83.304 | 64.5897 | 1621.6216 | 92.5% | 1500
12.5 | 0.040375 | 0.040375 | 110.145 | 82.9908 | 60.5627 | 1621.6216 | 92.5% | 1500
12.75 | 0.037778 | 0.037778 | 109.3683 | 82.4056 | 56.6672 | 1621.6216 | 92.5% | 1500
13 | 0.035274 | 0.035274 | 108.2452 | 81.5594 | 52.9114 | 1621.6216 | 92.5% | 1500
13.25 | 0.032868 | 0.032868 | 106.7925 | 80.4648 | 49.302 | 1621.6216 | 92.5% | 1500
13.5 | 0.030563 | 0.030563 | 105.0298 | 79.1367 | 45.844 | 1621.6216 | 92.5% | 1500
13.75 | 0.028361 | 0.028361 | 102.9785 | 77.5911 | 42.5412 | 1621.6216 | 92.5% | 1500
14 | 0.026264 | 0.026264 | 100.6616 | 75.8454 | 39.3959 | 1621.6216 | 92.5% | 1500
14.25 | 0.024273 | 0.024273 | 98.1036 | 73.918 | 36.4092 | 1621.6216 | 92.5% | 1500
14.5 | 0.022387 | 0.022387 | 95.33 | 71.8282 | 33.5812 | 1621.6216 | 92.5% | 1500
14.75 | 0.020607 | 0.020607 | 92.3667 | 69.5955 | 30.9108 | 1621.6216 | 92.5% | 1500
15 | 0.018931 | 0.018931 | 89.2402 | 67.2397 | 28.396 | 1621.6216 | 92.5% | 1500
15.25 | 0.017356 | 0.017356 | 85.9767 | 64.7807 | 26.0341 | 1621.6216 | 92.5% | 1500
15.5 | 0.015881 | 0.015881 | 82.6022 | 62.2382 | 23.8214 | 1621.6216 | 92.5% | 1500
15.75 | 0.014503 | 0.014503 | 79.1423 | 59.6313 | 21.7539 | 1621.6216 | 92.5% | 1500
16 | 0.013218 | 0.013218 | 75.6216 | 56.9785 | 19.827 | 1621.6216 | 92.5% | 1500
16.25 | 0.012024 | 0.012024 | 72.0638 | 54.2978 | 18.0355 | 1621.6216 | 92.5% | 1500
16.5 | 0.010916 | 0.010916 | 68.4912 | 51.606 | 16.374 | 1621.6216 | 92.5% | 1500
16.75 | 0.0098912 | 0.0098912 | 64.925 | 48.919 | 14.8367 | 1621.6216 | 92.5% | 1500
17 | 0.0089453 | 0.0089453 | 61.3847 | 46.2514 | 13.4179 | 1621.6216 | 92.5% | 1500
17.25 | 0.0080743 | 0.0080743 | 57.8882 | 43.6169 | 12.1114 | 1621.6216 | 92.5% | 1500
17.5 | 0.0072741 | 0.0072741 | 54.4519 | 41.0278 | 10.9111 | 1621.6216 | 92.5% | 1500
17.75 | 0.0065407 | 0.0065407 | 51.0904 | 38.495 | 9.811 | 1621.6216 | 92.5% | 1500
18 | 0.00587 | 0.00587 | 47.8167 | 36.0284 | 8.8051 | 1621.6216 | 92.5% | 1500
18.25 | 0.0052582 | 0.0052582 | 44.6418 | 33.6362 | 7.8872 | 1621.6216 | 92.5% | 1500
18.5 | 0.0047011 | 0.0047011 | 41.5754 | 31.3258 | 7.0517 | 1621.6216 | 92.5% | 1500
18.75 | 0.0041952 | 0.0041952 | 38.6253 | 29.1029 | 6.2927 | 1621.6216 | 92.5% | 1500
19 | 0.0037366 | 0.0037366 | 35.7978 | 26.9725 | 5.6049 | 1621.6216 | 92.5% | 1500
19.25 | 0.0033219 | 0.0033219 | 33.0977 | 24.9381 | 4.9828 | 1621.6216 | 92.5% | 1500
19.5 | 0.0029477 | 0.0029477 | 30.5284 | 23.0022 | 4.4215 | 1621.6216 | 92.5% | 1500
19.75 | 0.0026107 | 0.0026107 | 28.092 | 21.1664 | 3.9161 | 1621.6216 | 92.5% | 1500
20 | 0.002308 | 0.002308 | 25.7894 | 19.4315 | 3.462 | 1621.6216 | 92.5% | 1500
20.25 | 0.0020365 | 0.0020365 | 23.6203 | 17.7972 | 3.0548 | 1621.6216 | 92.5% | 1500
20.5 | 0.0017937 | 0.0017937 | 21.5836 | 16.2626 | 2.6905 | 1621.6216 | 92.5% | 1500
20.75 | 0.0015768 | 0.0015768 | 19.6771 | 14.8261 | 2.3653 | 1621.6216 | 92.5% | 1500
21 | 0.0013837 | 0.0013837 | 17.898 | 13.4856 | 2.0755 | 1621.6216 | 92.5% | 1500
21.25 | 0.0012119 | 0.0012119 | 16.2428 | 12.2384 | 1.8178 | 1621.6216 | 92.5% | 1500
21.5 | 0.0010595 | 0.0010595 | 14.7073 | 11.0815 | 1.5892 | 1621.6216 | 92.5% | 1500
21.75 | 0.00092455 | 0.00092455 | 13.287 | 10.0114 | 1.3868 | 1621.6216 | 92.5% | 1500
22 | 0.00080531 | 0.00080531 | 11.9771 | 9.0244 | 1.208 | 1621.6216 | 92.5% | 1500
22.25 | 0.00070016 | 0.00070016 | 10.7723 | 8.1166 | 1.0502 | 1621.6216 | 92.5% | 1500
22.5 | 0.00060763 | 0.00060763 | 9.6673 | 7.284 | 0.91144 | 1621.6216 | 92.5% | 1500
22.75 | 0.00052636 | 0.00052636 | 8.6566 | 6.5225 | 0.78954 | 1621.6216 | 92.5% | 1500
23 | 0.00045512 | 0.00045512 | 7.7345 | 5.8277 | 0.68269 | 1621.6216 | 92.5% | 1500
23.25 | 0.00039281 | 0.00039281 | 6.8956 | 5.1956 | 0.58922 | 1621.6216 | 92.5% | 1500
23.5 | 0.00033841 | 0.00033841 | 6.1344 | 4.6221 | 0.50762 | 1621.6216 | 92.5% | 1500
23.75 | 0.00029102 | 0.00029102 | 5.4454 | 4.1029 | 0.43653 | 1621.6216 | 92.5% | 1500
24 | 0.0002498 | 0.0002498 | 4.8234 | 3.6343 | 0.37471 | 1621.6216 | 92.5% | 1500
24.25 | 0.00021404 | 0.00021404 | 4.2633 | 3.2123 | 0.32106 | 1621.6216 | 92.5% | 1500
24.5 | 0.00018306 | 0.00018306 | 3.7602 | 2.8332 | 0.27459 | 1621.6216 | 92.5% | 1500
24.75 | 0.00015628 | 0.00015628 | 3.3095 | 2.4936 | 0.23443 | 1621.6216 | 92.5% | 1500
25 | 0.00013318 | 0.00013318 | 2.9066 | 2.19 | 0.19977 | 1621.6216 | 92.5% | 1500
25.25 | 0.00011329 | 0.00011329 | 2.5474 | 1.9194 | 0.16993 | 1621.6216 | 92.5% | 1500
25.5 | 9.6195e-05 | 9.6195e-05 | 2.2279 | 1.6786 | 0.14429 | 1621.6216 | 92.5% | 1500
25.75 | 8.1532e-05 | 8.1532e-05 | 1.9444 | 1.465 | 0.1223 | 1621.6216 | 92.5% | 1500
26 | 6.898e-05 | 6.898e-05 | 1.6934 | 1.2759 | 0 | 0 | #DIV/0! | 0
26.25 | 5.8255e-05 | 5.8255e-05 | 1.4718 | 1.1089 | 0 | 0 | #DIV/0! | 0
26.5 | 4.9109e-05 | 4.9109e-05 | 1.2765 | 0.9618 | 0 | 0 | #DIV/0! | 0
26.75 | 4.1325e-05 | 4.1325e-05 | 1.1048 | 0.83247 | 0 | 0 | #DIV/0! | 0
27 | 3.4712e-05 | 3.4712e-05 | 0.95432 | 0.71905 | 0 | 0 | #DIV/0! | 0
27.25 | 2.9105e-05 | 2.9105e-05 | 0.8226 | 0.61981 | 0 | 0 | #DIV/0! | 0
27.5 | 2.436e-05 | 2.436e-05 | 0.70762 | 0.53317 | 0 | 0 | #DIV/0! | 0
27.75 | 2.0352e-05 | 2.0352e-05 | 0.60747 | 0.45771 | 0 | 0 | #DIV/0! | 0
28 | 1.6974e-05 | 1.6974e-05 | 0.52043 | 0.39213 | 0 | 0 | #DIV/0! | 0
28.25 | 1.413e-05 | 1.413e-05 | 0.44497 | 0.33527 | 0 | 0 | #DIV/0! | 0
28.5 | 1.1742e-05 | 1.1742e-05 | 0.37967 | 0.28607 | 0 | 0 | #DIV/0! | 0
28.75 | 9.7405e-06 | 9.7405e-06 | 0.32331 | 0.2436 | 0 | 0 | #DIV/0! | 0
29 | 8.0656e-06 | 8.0656e-06 | 0.27476 | 0.20702 | 0 | 0 | #DIV/0! | 0
29.25 | 6.6667e-06 | 6.6667e-06 | 0.23303 | 0.17558 | 0 | 0 | #DIV/0! | 0
29.5 | 5.5007e-06 | 5.5007e-06 | 0.19724 | 0.14862 | 0 | 0 | #DIV/0! | 0
29.75 | 4.5305e-06 | 4.5305e-06 | 0.16662 | 0.12554 | 0 | 0 | #DIV/0! | 0
30 | 3.7249e-06 | 3.7249e-06 | 0.14047 | 0.10584 | 0 | 0 | #DIV/0! | 0
30.25 | 3.057e-06 | 3.057e-06 | 0.11819 | 0.089055 | 0 | 0 | #DIV/0! | 0
30.5 | 2.5044e-06 | 2.5044e-06 | 0.09925 | 0.074782 | 0 | 0 | #DIV/0! | 0
30.75 | 2.0481e-06 | 2.0481e-06 | 0.083178 | 0.062672 | 0 | 0 | #DIV/0! | 0
31 | 1.672e-06 | 1.672e-06 | 0.069572 | 0.05242 | 0 | 0 | #DIV/0! | 0
31.25 | 1.3625e-06 | 1.3625e-06 | 0.058077 | 0.043759 | 0 | 0 | #DIV/0! | 0
31.5 | 1.1083e-06 | 1.1083e-06 | 0.048386 | 0.036457 | 0 | 0 | #DIV/0! | 0
31.75 | 8.9997e-07 | 8.9997e-07 | 0.040233 | 0.030314 | 0 | 0 | #DIV/0! | 0
32 | 7.2949e-07 | 7.2949e-07 | 0.033388 | 0.025157 | 0 | 0 | #DIV/0! | 0
32.25 | 5.9027e-07 | 5.9027e-07 | 0.027654 | 0.020836 | 0 | 0 | #DIV/0! | 0
32.5 | 4.7677e-07 | 4.7677e-07 | 0.02286 | 0.017224 | 0 | 0 | #DIV/0! | 0
32.75 | 3.8441e-07 | 3.8441e-07 | 0.01886 | 0.014211 | 0 | 0 | #DIV/0! | 0
33 | 3.094e-07 | 3.094e-07 | 0.01553 | 0.011702 | 0 | 0 | #DIV/0! | 0
33.25 | 2.4858e-07 | 2.4858e-07 | 0.012763 | 0.0096169 | 0 | 0 | #DIV/0! | 0
33.5 | 1.9937e-07 | 1.9937e-07 | 0.010469 | 0.0078883 | 0 | 0 | #DIV/0! | 0
33.75 | 1.5962e-07 | 1.5962e-07 | 0.0085709 | 0.0064579 | 0 | 0 | #DIV/0! | 0
34 | 1.2757e-07 | 1.2757e-07 | 0.0070032 | 0.0052767 | 0 | 0 | #DIV/0! | 0
34.25 | 1.0177e-07 | 1.0177e-07 | 0.0057113 | 0.0043033 | 0 | 0 | #DIV/0! | 0
34.5 | 8.1051e-08 | 8.1051e-08 | 0.0046488 | 0.0035027 | 0 | 0 | #DIV/0! | 0
34.75 | 6.4435e-08 | 6.4435e-08 | 0.0037766 | 0.0028456 | 0 | 0 | #DIV/0! | 0
35 | 5.1135e-08 | 5.1135e-08 | 0.0030623 | 0.0023073 | 0 | 0 | #DIV/0! | 0
35.25 | 4.0509e-08 | 4.0509e-08 | 0.0024783 | 0.0018673 | 0 | 0 | #DIV/0! | 0
35.5 | 3.2035e-08 | 3.2035e-08 | 0.0020018 | 0.0015083 | 0 | 0 | #DIV/0! | 0
35.75 | 2.5289e-08 | 2.5289e-08 | 0.0016139 | 0.001216 | 0 | 0 | #DIV/0! | 0
36 | 1.9928e-08 | 1.9928e-08 | 0.0012987 | 0.0009785 | 0 | 0 | #DIV/0! | 0
36.25 | 1.5676e-08 | 1.5676e-08 | 0.001043 | 0.00078588 | 0 | 0 | #DIV/0! | 0
36.5 | 1.231e-08 | 1.231e-08 | 0.0008361 | 0.00062998 | 0 | 0 | #DIV/0! | 0
36.75 | 9.6497e-09 | 9.6497e-09 | 0.00066897 | 0.00050405 | 0 | 0 | #DIV/0! | 0
37 | 7.551e-09 | 7.551e-09 | 0.00053423 | 0.00040253 | 0 | 0 | #DIV/0! | 0
37.25 | 5.8984e-09 | 5.8984e-09 | 0.00042583 | 0.00032085 | 0 | 0 | #DIV/0! | 0
37.5 | 4.5994e-09 | 4.5994e-09 | 0.00033878 | 0.00025526 | 0 | 0 | #DIV/0! | 0
37.75 | 3.5802e-09 | 3.5802e-09 | 0.00026902 | 0.0002027 | 0 | 0 | #DIV/0! | 0
38 | 2.782e-09 | 2.782e-09 | 0.00021322 | 0.00016065 | 0 | 0 | #DIV/0! | 0
38.25 | 2.1579e-09 | 2.1579e-09 | 0.00016868 | 0.00012709 | 0 | 0 | #DIV/0! | 0
38.5 | 1.671e-09 | 1.671e-09 | 0.00013319 | 0.00010035 | 0 | 0 | #DIV/0! | 0
38.75 | 1.2916e-09 | 1.2916e-09 | 0.00010497 | 7.9092e-05 | 0 | 0 | #DIV/0! | 0
39 | 9.9663e-10 | 9.9663e-10 | 8.2575e-05 | 6.2217e-05 | 0 | 0 | #DIV/0! | 0
39.25 | 7.6767e-10 | 7.6767e-10 | 6.4836e-05 | 4.8852e-05 | 0 | 0 | #DIV/0! | 0
39.5 | 5.9028e-10 | 5.9028e-10 | 5.0813e-05 | 3.8286e-05 | 0 | 0 | #DIV/0! | 0
39.75 | 4.5309e-10 | 4.5309e-10 | 3.9748e-05 | 2.9949e-05 | 0 | 0 | #DIV/0! | 0
40 | 3.4718e-10 | 3.4718e-10 | 3.1035e-05 | 2.3384e-05 | 0 | 0 | #DIV/0! | 0