## 25F nomo
Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 041
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6701.8027
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 909.63 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2844.31 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2687.01 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3111.96 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2844.31 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3302.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 1627.61 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3614.84 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2879.85 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3611.61 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 775 | 3111.96 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2687.01 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 2177.35 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2879.85 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 3175.08 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3175.08 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 3302.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3582.49 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3270.15 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3622.76 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1000 | 460 | 3582.49 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 909.63 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3614.84 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1627.61 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 3592.24 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G7 | 525 | 140 | 2177.35 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3622.76 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G10 | 1000 | 140 | 3270.15 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 3611.61 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G13 | 1400 | 140 | 3592.24 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 041
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6367.9993
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1878.82 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2828.43 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2813.67 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3043.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2828.43 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3224.68 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 1760.56 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3529.4 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 3004.6 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3550.87 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 775 | 3043.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2813.67 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 2701.08 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3004.6 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 3210.84 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3210.84 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3224.68 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3522.96 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3368.33 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3545.48 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1000 | 460 | 3522.96 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1878.82 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3529.4 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1760.56 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 3542.14 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G7 | 525 | 140 | 2701.08 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3545.48 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G10 | 1000 | 140 | 3368.33 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 3550.87 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G13 | 1400 | 140 | 3542.14 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 041
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6076.482
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2012.25 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2741.98 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2771.93 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2960.39 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2741.98 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3142.67 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2588.15 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3460.88 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2932.8 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 3016.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2960.39 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2771.93 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2857.41 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2932.8 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3116.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3116.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3142.67 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3423.52 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3404.27 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 3099.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3423.52 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2012.25 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3460.88 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2588.15 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 3211.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2857.41 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3099.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3404.27 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 3016.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 3211.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 041
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4980.48
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2793.11 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2827.88 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2802.56 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2922.9 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2827.88 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2854.16 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2875.38 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3171.93 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2905.84 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1789.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2922.9 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2802.56 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3049.89 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2905.84 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3070.34 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3070.34 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2854.16 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3148.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3303.34 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1891.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3148.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2793.11 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3171.93 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2875.38 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 2003.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3049.89 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1891.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3303.34 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1400 | 775 | 1789.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2003.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 041
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4636.7787
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2660.26 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2446.44 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2678.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2572.14 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2446.44 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2775.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2535.4 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3072.29 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2549.46 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1597.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2572.14 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2678.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2733.34 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2549.46 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2768.02 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2768.02 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2775.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3052.87 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3032.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1700.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3052.87 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2660.26 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3072.29 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2535.4 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 1803.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2733.34 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1700.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3032.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1597.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1803.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
G0 | 909.63 | 1878.82 | 2012.25 | 2793.11 | 2660.26
G1 | 2687.01 | 2813.67 | 2771.93 | 2802.56 | 2678.06 | Season/Year: | WINTER 2009
G2 | 2844.31 | 2828.43 | 2741.98 | 2827.88 | 2446.44 | Direction: | South-to-North (SN)
G3 | 1627.61 | 1760.56 | 2588.15 | 2875.38 | 2535.4 | Case Loads: | Heavy Loads
G4 | 2879.85 | 3004.6 | 2932.8 | 2905.84 | 2549.46 | Outage: | 041
G5 | 3111.96 | 3043.24 | 2960.39 | 2922.9 | 2572.14 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2177.35 | 2701.08 | 2857.41 | 3049.89 | 2733.34 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3175.08 | 3210.84 | 3116.86 | 3070.34 | 2768.02 | Study Person: | JGO7470
G8 | 3302.86 | 3224.68 | 3142.67 | 2854.16 | 2775.2 | Source: | 041WINTER09v1SNH
G9 | 3270.15 | 3368.33 | 3404.27 | 3303.34 | 3032.42
G10 | 3582.49 | 3522.96 | 3423.52 | 3148.71 | 3052.87
G11 | 3614.84 | 3529.4 | 3460.88 | 3171.93 | 3072.29
G12 | 3592.24 | 3542.14 | 3211.16 | 2003.61 | 1803.64
G13 | 3622.76 | 3545.48 | 3099.15 | 1891.38 | 1700.59
G14 | 3611.61 | 3550.87 | 3016.95 | 1789.3 | 1597.02
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 041 | Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6701.8027 | 909.63 | 2687.01 | 2844.31 | 1627.61 | 2879.85 | 3111.96 | 2177.35 | 3175.08 | 3302.86 | 3270.15 | 3582.49 | 3614.84 | 3592.24 | 3622.76 | 3611.61
35F | 6367.9993 | 1878.82 | 2813.67 | 2828.43 | 1760.56 | 3004.6 | 3043.24 | 2701.08 | 3210.84 | 3224.68 | 3368.33 | 3522.96 | 3529.4 | 3542.14 | 3545.48 | 3550.87
45F | 6076.482 | 2012.25 | 2771.93 | 2741.98 | 2588.15 | 2932.8 | 2960.39 | 2857.41 | 3116.86 | 3142.67 | 3404.27 | 3423.52 | 3460.88 | 3211.16 | 3099.15 | 3016.95
60F | 4980.48 | 2793.11 | 2802.56 | 2827.88 | 2875.38 | 2905.84 | 2922.9 | 3049.89 | 3070.34 | 2854.16 | 3303.34 | 3148.71 | 3171.93 | 2003.61 | 1891.38 | 1789.3
70F | 4636.7787 | 2660.26 | 2678.06 | 2446.44 | 2535.4 | 2549.46 | 2572.14 | 2733.34 | 2768.02 | 2775.2 | 3032.42 | 3052.87 | 3072.29 | 1803.64 | 1700.59 | 1597.02

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 909.46 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -4.52 | -541.58 | -541.62 | 6680.29 | 909.63 | -696.7 | FULL
G1 | 2687.48 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.79 | 534.23 | 534.42 | 6685.87 | 2687.01 | -1699.75 | CTG_FAIL_IN_FULL
G2 | 2843.09 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 16.65 | 835.6 | 835.72 | 6701.95 | 2844.31 | -1771.18 | CTG_FAIL_IN_FULL
G3 | 1627.76 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | -4.57 | -541.69 | -541.8 | 6696.83 | 1627.61 | -1046.17 | FULL
G4 | 2880.3 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.79 | 535.04 | 535.25 | 6686.72 | 2879.85 | -1751.79 | CTG_FAIL_IN_FULL
G5 | 3112.46 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2667.01 | -2666.92 | 6710.96 | 3111.96 | -1851.51 | CTG_FAIL_IN_FULL
G6 | 2178.16 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | -4.57 | -524.51 | -546.5 | 6712.27 | 2177.35 | -1261.54 | FULL
G7 | 3175.21 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.79 | 535.04 | 535 | 6688.08 | 3175.08 | -1802.01 | CTG_FAIL_IN_FULL
G8 | 3304.22 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2681.61 | -2681.93 | 6703.86 | 3302.86 | -1842.07 | CTG_FAIL_IN_FULL
G9 | 3270.73 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.79 | 536.28 | 536.44 | 6744.56 | 3270.15 | -1689.83 | CTG_FAIL_IN_FULL
G10 | 3583.05 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2678.21 | -2678.15 | 6688.73 | 3582.49 | -1837.49 | CTG_FAIL_IN_FULL
G11 | 3615.43 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2689.84 | -2689.78 | 6697.98 | 3614.84 | -1828.85 | CTG_FAIL_IN_FULL
G12 | 3590.5 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3549.33 | 3551.1 | 6755.27 | 3592.24 | -1729.94 | FULL
G13 | 3621.64 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3583.81 | 3581.98 | 6681.86 | 3622.76 | -1707.9 | FULL
G14 | 3612.82 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3575.33 | 3573.74 | 6691.81 | 3611.61 | -1665.98 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1878.94 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -4.52 | -535.8 | -535.84 | 6375.36 | 1878.82 | -1225.96 | FULL
G1 | 2814.85 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.79 | 517.58 | 517.44 | 6353.37 | 2813.67 | -1735.71 | CTG_FAIL_IN_FULL
G2 | 2828.48 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 16.65 | 814.39 | 814.36 | 6362.24 | 2828.43 | -1722.63 | CTG_FAIL_IN_FULL
G3 | 1760.57 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -4.52 | -522.94 | -523.01 | 6368.06 | 1760.56 | -1091.37 | FULL
G4 | 3005.75 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.79 | 518.52 | 518.37 | 6354.77 | 3004.6 | -1785.24 | CTG_FAIL_IN_FULL
G5 | 3043.06 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2603.27 | -2603.12 | 6365.24 | 3043.24 | -1779.09 | CTG_FAIL_IN_FULL
G6 | 2701.19 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -4.52 | -528.44 | -528.37 | 6398.23 | 2701.08 | -1519.48 | FULL
G7 | 3210.95 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2603.27 | -2603.19 | 6351.86 | 3210.84 | -1782.61 | CTG_FAIL_IN_FULL
G8 | 3225.33 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2596.44 | -2596.35 | 6362.25 | 3224.68 | -1767.27 | CTG_FAIL_IN_FULL
G9 | 3368.63 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.79 | 517.9 | 517.91 | 6413.99 | 3368.33 | -1705.65 | CTG_FAIL_IN_FULL
G10 | 3523.26 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2606.81 | -2606.8 | 6347.86 | 3522.96 | -1765.09 | CTG_FAIL_IN_FULL
G11 | 3529.78 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2594.65 | -2594.68 | 6359.29 | 3529.4 | -1743.44 | CTG_FAIL_IN_FULL
G12 | 3543.11 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3507.34 | 3510.17 | 6415.01 | 3542.14 | -1655.03 | FULL
G13 | 3548.58 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3513.76 | 3516.28 | 6342.63 | 3545.48 | -1628.74 | FULL
G14 | 3551.21 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3516.92 | 3519.28 | 6349.83 | 3550.87 | -1601.91 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2012.4 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -4.52 | -518.15 | -518.24 | 6096.73 | 2012.25 | -1304.25 | FULL
G1 | 2772.64 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 16.65 | 786.67 | 786.71 | 6063.68 | 2771.93 | -1703.24 | CTG_FAIL_IN_FULL
G2 | 2742.42 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 16.65 | 785.59 | 785.69 | 6069.58 | 2741.98 | -1653.48 | CTG_FAIL_IN_FULL
G3 | 2588.2 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.79 | 505.11 | 505.03 | 6114.98 | 2588.15 | -1574.52 | CTG_FAIL_IN_FULL
G4 | 2933.14 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2531.59 | -2531.35 | 6062.34 | 2932.8 | -1730.06 | CTG_FAIL_IN_FULL
G5 | 2960.77 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2533.05 | -2532.76 | 6072.41 | 2960.39 | -1714.12 | CTG_FAIL_IN_FULL
G6 | 2857.71 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.79 | 501.97 | 501.96 | 6115.12 | 2857.41 | -1594.26 | CTG_FAIL_IN_FULL
G7 | 3117.34 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2532.15 | -2531.93 | 6058.07 | 3116.86 | -1717.02 | CTG_FAIL_IN_FULL
G8 | 3143.23 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2532.4 | -2532.21 | 6068.24 | 3142.67 | -1700.7 | CTG_FAIL_IN_FULL
G9 | 3406.09 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2535.74 | -2536.99 | 6126.77 | 3404.27 | -1719.45 | CTG_FAIL_IN_FULL
G10 | 3423.87 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2532.58 | -2532.45 | 6055.07 | 3423.52 | -1697.51 | CTG_FAIL_IN_FULL
G11 | 3461.11 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2539.43 | -2539.36 | 6065.83 | 3460.88 | -1684.21 | CTG_FAIL_IN_FULL
G12 | 3211.3 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -434.25 | -434.22 | 6108.19 | 3211.16 | -1453.37 | FULL
G13 | 3099.68 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -436.12 | -436.17 | 6032.33 | 3099.15 | -1340.63 | FULL
G14 | 3017.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -433.67 | -433.52 | 6037.89 | 3016.95 | -1265.78 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2793.48 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2409.68 | -2409.39 | 5037.44 | 2793.11 | -1627.82 | CTG_FAIL_IN_FULL
G1 | 2802.44 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2399.07 | -2398.77 | 4967.84 | 2802.56 | -1595.51 | CTG_FAIL_IN_FULL
G2 | 2829.14 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2410.8 | -2409.87 | 4978.08 | 2827.88 | -1590.07 | CTG_FAIL_IN_FULL
G3 | 2875.57 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2400.81 | -2400.5 | 5036.72 | 2875.38 | -1622.06 | CTG_FAIL_IN_FULL
G4 | 2905.71 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2410.36 | -2410.07 | 4964.46 | 2905.84 | -1599.46 | CTG_FAIL_IN_FULL
G5 | 2923.46 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2411 | -2410.24 | 4975.94 | 2922.9 | -1582.89 | CTG_FAIL_IN_FULL
G6 | 3050.04 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2398.28 | -2398.1 | 5032.76 | 3049.89 | -1613.18 | CTG_FAIL_IN_FULL
G7 | 3070.2 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2392.79 | -2392.57 | 4963.05 | 3070.34 | -1579.25 | CTG_FAIL_IN_FULL
G8 | 2855.38 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2218.03 | -2219.44 | 4968.86 | 2854.16 | -1414.89 | FULL
G9 | 3303.65 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3273.68 | 3274.18 | 5031.99 | 3303.34 | -1538.87 | FULL
G10 | 3149.29 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2239.35 | -2240.4 | 4958.29 | 3148.71 | -1420.62 | FULL
G11 | 3172.4 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2243.21 | -2241.26 | 4970.15 | 3171.93 | -1403.06 | FULL
G12 | 2003.65 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -424.24 | -424.18 | 4984.12 | 2003.61 | -629.6 | FULL
G13 | 1893.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -422.78 | -422.87 | 4912.84 | 1891.38 | -531.99 | FULL
G14 | 1789.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -421.99 | -421.93 | 4924.66 | 1789.3 | -441.38 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2660.14 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2297.53 | -2297.18 | 4693.82 | 2660.26 | -1514.08 | CTG_FAIL_IN_FULL
G1 | 2678.43 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2297.01 | -2296.34 | 4623.47 | 2678.06 | -1493.61 | CTG_FAIL_IN_FULL
G2 | 2446.69 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2121.64 | -2119.57 | 4629.89 | 2446.44 | -1329.33 | FULL
G3 | 2535.58 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2146.35 | -2148.34 | 4685.61 | 2535.4 | -1389.46 | FULL
G4 | 2549.76 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2137.3 | -2138.29 | 4616.27 | 2549.46 | -1357.2 | FULL
G5 | 2571.47 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2149.94 | -2151.31 | 4626.53 | 2572.14 | -1344.57 | FULL
G6 | 2735.04 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2147.83 | -2146.21 | 4684.97 | 2733.34 | -1375.22 | FULL
G7 | 2770.38 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2174.21 | -2172.98 | 4614.56 | 2768.02 | -1372.21 | FULL
G8 | 2776.96 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2153.7 | -2152.38 | 4627.87 | 2775.2 | -1339.54 | FULL
G9 | 3032.81 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2139.76 | -2138.11 | 4687.54 | 3032.42 | -1344.59 | FULL
G10 | 3053.28 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2142.61 | -2141.21 | 4618.26 | 3052.87 | -1326.52 | FULL
G11 | 3072.8 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2143.84 | -2141.84 | 4631.06 | 3072.29 | -1308.12 | FULL
G12 | 1803.1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -425.1 | -425.06 | 4646.09 | 1803.64 | -483.58 | FULL
G13 | 1698.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -424.38 | -424.33 | 4576.44 | 1700.59 | -391.58 | FULL
G14 | 1596.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -423.7 | -423.66 | 4589.3 | 1597.02 | -299.98 | FULL
041WINTER09v1SNH