## 25F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 023
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6629.1333
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 115.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 251.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 189.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 873.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 251.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 1835.98 | N-2: Maple Valley-Sammamish-Klahanie & Monroe-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 729.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1578.64 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 799.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1208.14 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 873.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 189.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1497.56 | N-2: Maple Valley-Sammamish-Klahanie & Sammamish-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 799.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 1686.07 | N-2: Maple Valley-Sammamish-Klahanie & Sammamish-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1686.07 | N-2: Maple Valley-Sammamish-Klahanie & Sammamish-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1835.98 | N-2: Maple Valley-Sammamish-Klahanie & Monroe-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1456.12 | N-2: Maple Valley-Sammamish-Klahanie & Monroe-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1259.87 | N-2: Maple Valley-Sammamish-Klahanie & Sammamish-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1198.39 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1456.12 | N-2: Maple Valley-Sammamish-Klahanie & Monroe-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 115.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1578.64 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 729.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 1051.18 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1497.56 | N-2: Maple Valley-Sammamish-Klahanie & Sammamish-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1198.39 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1259.87 | N-2: Maple Valley-Sammamish-Klahanie & Sammamish-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1208.14 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1051.18 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 023
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6296.216
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 341.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 481.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 413.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1075.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 481.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 1780.17 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 930.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1460.38 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 1005.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1027.59 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1075.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 413.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1494.84 | N-2: Maple Valley-Sammamish-Klahanie & Sammamish-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1005.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 1687.1 | N-2: Maple Valley-Sammamish-Klahanie & Monroe-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1687.1 | N-2: Maple Valley-Sammamish-Klahanie & Monroe-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1780.17 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1382.22 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1246.36 | N-2: Maple Valley-Sammamish-Klahanie & Monroe-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1042.04 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1382.22 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 341.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1460.38 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 930.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 960.01 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1494.84 | N-2: Maple Valley-Sammamish-Klahanie & Sammamish-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1042.04 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1246.36 | N-2: Maple Valley-Sammamish-Klahanie & Monroe-Novelty 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1027.59 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 960.01 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 023
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6010.5027
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 186.48 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 321.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 256.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 890.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 321.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 1623.33 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 749.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1329.79 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 824.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 944.84 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 890.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 256.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1442.13 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 824.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 1537.42 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1537.42 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1623.33 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1227.96 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1157.1 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 953.83 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1227.96 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 186.48 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1329.79 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 749.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 872.25 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1442.13 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 953.83 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1157.1 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 944.84 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 872.25 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 023
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4936.6593
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1025.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1165.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1099.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1627.77 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1165.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 1442.12 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1484.25 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 922.46 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 1543.54 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 486.91 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1627.77 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 1099.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1282.96 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1543.54 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1369.09 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1369.09 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1442.12 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 938.19 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 778.17 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 546.24 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 938.19 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1025.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 922.46 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1484.25 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 451.74 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1282.96 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 546.24 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 778.17 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 486.91 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 451.74 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 023
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4601.8107
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1185.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1330.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1262.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1490.95 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1330.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 1293.16 | N-1: Monroe - HRNCHTAP MS | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1324.6 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 745.45 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 1411.6 | N-1: Monroe - HRNCHTAP MS | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 294.5 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1490.95 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1262.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1145.01 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1411.6 | N-1: Monroe - HRNCHTAP MS | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1233.17 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1233.17 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1293.16 | N-1: Monroe - HRNCHTAP MS | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 725.2 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 643.86 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 369.1 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 725.2 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1185.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 745.45 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1324.6 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 331.21 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1145.01 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 369.1 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 643.86 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 294.5 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 331.21 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
G0 | 115.97 | 341.63 | 186.48 | 1025.09 | 1185.51
G1 | 189.97 | 413.92 | 256.28 | 1099.58 | 1262.21 | Season/Year: | WINTER 2009
G2 | 251.09 | 481.82 | 321.36 | 1165.22 | 1330.08 | Direction: | North-to-South (NS)
G3 | 729.27 | 930.9 | 749.38 | 1484.25 | 1324.6 | Case Loads: | Heavy Loads
G4 | 799.09 | 1005.29 | 824.41 | 1543.54 | 1411.6 | Outage: | 023
G5 | 873.99 | 1075.2 | 890.3 | 1627.77 | 1490.95 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 1497.56 | 1494.84 | 1442.13 | 1282.96 | 1145.01 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 1686.07 | 1687.1 | 1537.42 | 1369.09 | 1233.17 | Study Person: | FRP9899
G8 | 1835.98 | 1780.17 | 1623.33 | 1442.12 | 1293.16 | Source: | 023WINTER09v2NSH
G9 | 1259.87 | 1246.36 | 1157.1 | 778.17 | 643.86
G10 | 1456.12 | 1382.22 | 1227.96 | 938.19 | 725.2
G11 | 1578.64 | 1460.38 | 1329.79 | 922.46 | 745.45
G12 | 1051.18 | 960.01 | 872.25 | 451.74 | 331.21
G13 | 1198.39 | 1042.04 | 953.83 | 546.24 | 369.1
G14 | 1208.14 | 1027.59 | 944.84 | 486.91 | 294.5
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 023 | Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6629.1333 | 115.97 | 189.97 | 251.09 | 729.27 | 799.09 | 873.99 | 1497.56 | 1686.07 | 1835.98 | 1259.87 | 1456.12 | 1578.64 | 1051.18 | 1198.39 | 1208.14
35F | 6296.216 | 341.63 | 413.92 | 481.82 | 930.9 | 1005.29 | 1075.2 | 1494.84 | 1687.1 | 1780.17 | 1246.36 | 1382.22 | 1460.38 | 960.01 | 1042.04 | 1027.59
45F | 6010.5027 | 186.48 | 256.28 | 321.36 | 749.38 | 824.41 | 890.3 | 1442.13 | 1537.42 | 1623.33 | 1157.1 | 1227.96 | 1329.79 | 872.25 | 953.83 | 944.84
60F | 4936.6593 | 1025.09 | 1099.58 | 1165.22 | 1484.25 | 1543.54 | 1627.77 | 1282.96 | 1369.09 | 1442.12 | 778.17 | 938.19 | 922.46 | 451.74 | 546.24 | 486.91
70F | 4601.8107 | 1185.51 | 1262.21 | 1330.08 | 1324.6 | 1411.6 | 1490.95 | 1145.01 | 1233.17 | 1293.16 | 643.86 | 725.2 | 745.45 | 331.21 | 369.1 | 294.5

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 114.88 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 472.64 | 472.38 | 6661.12 | 115.97 | 0 | FULL
G1 | 188.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 472.98 | 472.75 | 6586.8 | 189.97 | 0 | FULL
G2 | 250.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 472.68 | 472.42 | 6595.95 | 251.09 | 0 | FULL
G3 | 728.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 482.18 | 482.12 | 6653.43 | 729.27 | 0 | FULL
G4 | 798.85 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 482.49 | 482.42 | 6583.13 | 799.09 | 0 | FULL
G5 | 873.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 482.82 | 482.55 | 6595 | 873.99 | 0 | FULL
G6 | 1500.3 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | N-2: Maple Valley-Sammamish-Klahanie & Sammamish-Novelty 230kV | -14.2 | -506.5 | -506.38 | 6667.68 | 1497.56 | 0 | FULL
G7 | 1689.54 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | N-2: Maple Valley-Sammamish-Klahanie & Sammamish-Novelty 230kV | -14.2 | -505.48 | -505.69 | 6604.13 | 1686.07 | 0 | FULL
G8 | 1840.97 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | N-2: Maple Valley-Sammamish-Klahanie & Monroe-Novelty 230kV | -14.2 | -506.91 | -506.86 | 6622.34 | 1835.98 | 0 | FULL
G9 | 1261.37 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | N-2: Maple Valley-Sammamish-Klahanie & Sammamish-Novelty 230kV | -14.2 | -505.87 | -505.84 | 6677.18 | 1259.87 | 0 | FULL
G10 | 1459.21 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | N-2: Maple Valley-Sammamish-Klahanie & Monroe-Novelty 230kV | -14.2 | -506.5 | -506.2 | 6614.66 | 1456.12 | 0 | FULL
G11 | 1581.78 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 655.89 | 656.06 | 6634.09 | 1578.64 | 0 | FULL
G12 | 1053.66 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: Snohomish 230kV Bus Sect #4 | -26.88 | -747.23 | -747.16 | 6684.36 | 1051.18 | 0 | FULL
G13 | 1200.56 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.08 | -761.51 | -761.13 | 6621 | 1198.39 | 0 | FULL
G14 | 1209.22 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #1 | -13.49 | -530.23 | -530.52 | 6636.13 | 1208.14 | 0 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 340.42 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 467.72 | 467.59 | 6323.39 | 341.63 | 0 | FULL
G1 | 412.28 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 467.42 | 467.32 | 6250.87 | 413.92 | 0 | FULL
G2 | 481.86 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 467.65 | 467.52 | 6261.55 | 481.82 | 0 | FULL
G3 | 931 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 475.34 | 475.17 | 6321.74 | 930.9 | 0 | FULL
G4 | 1005.65 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 475.46 | 475.29 | 6251.79 | 1005.29 | 0 | FULL
G5 | 1076.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 475.56 | 475.45 | 6265.21 | 1075.2 | 0 | FULL
G6 | 1497.57 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | N-2: Maple Valley-Sammamish-Klahanie & Sammamish-Novelty 230kV | -14.2 | -495.29 | -495.2 | 6335.76 | 1494.84 | 0 | FULL
G7 | 1692.14 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | N-2: Maple Valley-Sammamish-Klahanie & Monroe-Novelty 230kV | -14.2 | -494.51 | -494.55 | 6273.24 | 1687.1 | 0 | FULL
G8 | 1785.96 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 630.18 | 629.87 | 6290.9 | 1780.17 | 0 | FULL
G9 | 1249.01 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | N-2: Maple Valley-Sammamish-Klahanie & Monroe-Novelty 230kV | -14.2 | -496.87 | -496.77 | 6345.75 | 1246.36 | 0 | FULL
G10 | 1384.15 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 630.53 | 630.71 | 6282.34 | 1382.22 | 0 | FULL
G11 | 1462.01 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #1 | -13.49 | -513.71 | -513.59 | 6300.48 | 1460.38 | 0 | FULL
G12 | 959.86 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.08 | -740.21 | -739.62 | 6351.41 | 960.01 | 0 | FULL
G13 | 1042.33 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.08 | -740.33 | -740.38 | 6287.06 | 1042.04 | 0 | FULL
G14 | 1028.56 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #1 | -13.49 | -514.63 | -514.51 | 6301.75 | 1027.59 | 0 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 184.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 434.12 | 434.06 | 6039.05 | 186.48 | 0 | FULL
G1 | 255.18 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 434.25 | 434.18 | 5966.76 | 256.28 | 0 | FULL
G2 | 319.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 434.22 | 434.16 | 5977.45 | 321.36 | 0 | FULL
G3 | 747.37 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 439.48 | 439.55 | 6035.5 | 749.38 | 0 | FULL
G4 | 824.11 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 439.92 | 439.6 | 5965.96 | 824.41 | 0 | FULL
G5 | 890.2 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 439.64 | 439.72 | 5979.24 | 890.3 | 0 | FULL
G6 | 1445.37 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 593.51 | 593.26 | 6050.94 | 1442.13 | 0 | FULL
G7 | 1540.33 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 594.33 | 594.21 | 5985.54 | 1537.42 | 0 | FULL
G8 | 1627.27 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 594.13 | 593.82 | 6002.87 | 1623.33 | 0 | FULL
G9 | 1158.22 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 594.74 | 594.33 | 6059.9 | 1157.1 | 0 | FULL
G10 | 1229.54 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 593.48 | 593.53 | 5994.61 | 1227.96 | 0 | FULL
G11 | 1332.73 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 595.11 | 595.22 | 6013.46 | 1329.79 | 0 | FULL
G12 | 872.53 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.08 | -719.86 | -719.48 | 6066.46 | 872.25 | 0 | FULL
G13 | 954.56 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.08 | -720.06 | -720.13 | 6002.31 | 953.83 | 0 | FULL
G14 | 947.35 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #1 | -13.49 | -502.01 | -502.17 | 6017.49 | 944.84 | 0 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1025.56 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 440.32 | 440.55 | 4958.56 | 1025.09 | 0 | FULL
G1 | 1100.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 440.44 | 440.69 | 4892.39 | 1099.58 | 0 | FULL
G2 | 1166.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 440.57 | 440.75 | 4908.96 | 1165.22 | 0 | FULL
G3 | 1485.18 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 539.32 | 539.51 | 4970.03 | 1484.25 | 0 | FULL
G4 | 1547.16 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Mon - Snoh - Horse Rnch 230kV | 18.63 | 545.46 | 545.71 | 4904.98 | 1543.54 | 0 | FULL
G5 | 1630.96 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Mon - Snoh - Horse Rnch 230kV | 18.63 | 545.15 | 545.63 | 4924.66 | 1627.77 | 0 | FULL
G6 | 1286.29 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | 3TM: Mon - Snoh - Horse Rnch 230kV | 18.63 | 545.64 | 545.89 | 4972.03 | 1282.96 | 0 | FULL
G7 | 1371.92 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 545.92 | 546.19 | 4909.42 | 1369.09 | 0 | FULL
G8 | 1444.28 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 544.1 | 544.57 | 4929.09 | 1442.12 | 0 | FULL
G9 | 778.26 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 21.84 | 541.22 | 541.49 | 4978.74 | 778.17 | 0 | FULL
G10 | 939.72 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #1 | -13.49 | -473.67 | -473.54 | 4918.01 | 938.19 | 0 | FULL
G11 | 923.17 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #1 | -13.49 | -477.12 | -477.14 | 4934.56 | 922.46 | 0 | FULL
G12 | 452.07 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.08 | -681.67 | -681.26 | 4986.49 | 451.74 | 0 | FULL
G13 | 545.98 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.08 | -685.59 | -685.21 | 4922.87 | 546.24 | 0 | FULL
G14 | 486.41 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.44 | 470.54 | 470.5 | 4939.1 | 486.91 | 0 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1186.67 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 441.11 | 441.35 | 4627.52 | 1185.51 | 0 | FULL
G1 | 1263.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 442.1 | 442.05 | 4562.67 | 1262.21 | 0 | FULL
G2 | 1333.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 442.15 | 442.27 | 4581.27 | 1330.08 | 0 | FULL
G3 | 1325.8 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 504.04 | 504.33 | 4632.44 | 1324.6 | 0 | FULL
G4 | 1413.04 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | N-1: Monroe - HRNCHTAP MS | 18.54 | 505.52 | 506.04 | 4569.66 | 1411.6 | 0 | FULL
G5 | 1493.77 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | 3TM: Mon - Snoh - Horse Rnch 230kV | 18.63 | 505.48 | 505.93 | 4588.96 | 1490.95 | 0 | FULL
G6 | 1146.96 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 498.97 | 498.98 | 4635.79 | 1145.01 | 0 | FULL
G7 | 1233.26 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.63 | 501.22 | 501.74 | 4573.69 | 1233.17 | 0 | FULL
G8 | 1294.2 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | N-1: Monroe - HRNCHTAP MS | 18.54 | 504.93 | 505.35 | 4592.76 | 1293.16 | 0 | FULL
G9 | 643.36 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 21.84 | 504.21 | 504.3 | 4642.28 | 643.86 | 0 | FULL
G10 | 724.4 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 21.84 | 501.26 | 501.81 | 4579.67 | 725.2 | 0 | FULL
G11 | 744.81 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.44 | 462.43 | 462.65 | 4598.81 | 745.45 | 0 | FULL
G12 | 329.88 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.08 | -665.36 | -665.14 | 4650.97 | 331.21 | 0 | FULL
G13 | 367.86 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #1 | -13.49 | -463.41 | -463.3 | 4587.62 | 369.1 | 0 | FULL
G14 | 293.27 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.44 | 461.79 | 462.3 | 4603.05 | 294.5 | 0 | FULL
023WINTER09v2NSH