November 21, 1997PROJECT NUMBER

Contract # TW-0928AQ-1486ADATENovember 20, 1997

SPECIALSTANDARD SPECIFICATION

SECTION 162676-S

VARIABLE FREQUENCY DRIVE FOR VARIABLE

TORQUE PUMP OR FAN ALTERNATING CURRENT MOTORS

Page

PART 1 - GENERAL

1.01 	Description of Work

1.02 	References

1.03 	Submittals

1.04 	Quality Assurance

1.05 	Warranty

PART 2 - PRODUCTS

2.01 	General

2.02 	VFD Supplied with New Pump or Fan System

2.03 	VFD Supplied For Existing Pump or Fan System

2.04 	VFD Maximum Voltage and Current Harmonic Distortion

2.05 	Enclosure

2.06 	Design Feature Minimum Requirements

2.07 	Protective Features

2.08 	Diagnostic Fault Indicators

2.09 	VFD Environmental and Service Conditions

2.10 	VFD Motor Requirements

2.11 	Source Quality Control

2.12 	Spare Parts

2.13 	Test And Inspection Equipment

PART 3 - EXECUTION

3.01	Examination

3.02	Preparation

3.03	Installation

3.04	Field Quality Control

SPECIALSTANDARD SPECIFICATION

SECTION 162676

VARIABLE FREQUENCY DRIVE FOR VARIABLE

TORQUE PUMP OR FAN ALTERNATING CURRENT MOTORS

PART 1 - GENERALPART I - GENERAL

1.01	DESCRIPTION OF WORK

A.	Furnish and install complete Variable Frequency Drive (VFD) system as described in this Section, and as detailed on Drawings.  VFD will be used to control speed of three-phase variable torque pump or fan alternating current (AC) induction motor.

B.	Provide services of VFD manufacturer’s service engineer to perform the following:

1.	Test, checkout, and start up VFD system.  Contractor shall provide necessary test equipment to collect data required under “Field Quality Control” Article.

2.	Train Sandia National Laboratories’ (SNL) personnel in proper operation and maintenance of VFD system in accordance with Part 3 of Division 15, Section “Mechanical Systems Demonstration.”

Training shall include minimum of four hours of on-site instruction for new equipment, unless otherwise noted in Contract documents.

3.	Contractor shall coordinate testing, checkout, start-up, and training functions with appropriate SNL Maintenance organization, which shall include:.

a.	Loss of speed reference signal selectable options.

b.	Energy-saving optimization, such as low voltage for lighter loads.

C.	Related Sections:  Refer to the following sections for related work:

Division 1, Section 1300-S, “Descriptive Submittals”

Division 1, Section “Contract Closeout”

Division 15, Section  “Mechanical Systems Demonstrations”

Division 16, Section “ Electrical Work”

1.02	REFERENCES

A.	Code of Federal Regulations (CFR)

Title 10 Part 435	Mandatory Energy Conservation Standards for Federal Buildings

Title 29 Part 1910	Occupational Safety and Health Standards for General Industry

Title 29 Part 1926	Safety and Health Standards for Construction

B.	Institute of Electrical and Electronics Engineers (IEEE )

112	Test Procedures for Polyphase Induction Machines

399	IEEE Recommended Practice for Industrial and Commercial Power Systems Analysis

519	IEEE Recommended Practices and Requirements for Harmonic Control in Electrical Power Systems

C.	National Electrical Manufacturers Association (NEMA)

250	Enclosures for Electrical Equipment (1000 Volts Maximum)

ICS 1	General Standards for Industrial Control and Systems

ICS 1.1	Safety Guidelines for the Application, Installation and Maintenance of Solid State Control

ICS 6	Enclosures for Industrial Controls and Systems

MG 1	Motors and Generators

MG 2	Safety Standards for Construction and Guide for Selection, Installation and Use of Electric Motors and Generators

MG10	Energy Guide for Selection and Use of Polyphase Motors

D.	National Fire Protection Association (NFPA)

70	National Electrical Code

E.	Underwriters Laboratories Inc. (UL)

508C	Power Conversion Equipment

1.03	SUBMITTALS

A.	Equipment Submittals:  Submit in accordance with provisions ofconditions of Contract and Division 1, Section 1300-S, “Descriptive Submittals,” except as noted herein.  Include the following:

1.	Shop drawings depicting applicable schematic diagrams.

2.	Description list of equipment features to demonstrate compliance with requirements of Part 2.

3.	Written certification from VFD manufacturer that VFD system will not exceed maximum harmonic distortion limits. Clearly identify modifications to manufacturer’s standard VFD system which are taken to meet limit requirements.

4.	If VFD submitted is other than that specified on Drawings, submit harmonic distortion analysis per applicable requirements of Part 2.

5.	Prior to substantial completion of Contract, submit final documentation for VFD installation.

B.	Record Document Submittals:  Comply with requirements of Division 1, Section  “Project Closeout,” except as noted herein.  Include the following:

1.	Final Drawings:  Provide one set of reproducible drawings of black on white 11 by 17 inch (280 by 425 mm) size or in computer format, showing dimensions, details, wiring diagrams, and interconnections that reflect “as-built” Work.

a.	Drawings of sufficiently high-quality drafting and reproducibility as to permit microfilming or scanning.

b.	Include wiring for subsystems.

c.	Lay out internal wiring diagrams such that terminal blocks for external connections have sufficient room, minimum of 1-1/2 inch (38.1 mm), for showing cables for external connections.

d.	Should Drawings be submitted in computer disk format, prior approval from SDR must be obtained to ensure compatibility with SNL’s CADD standard software.

2.	VFD Standard Drawings:  Provide minimum of three (3) complete sets of VFD supplier’s standard drawings showing schematics, wiring, outline dimensions, mounting details, and equipment weight.

3.	Instruction Books and Spare Parts List:  Provide minimum of three (3) copies of instruction books, operating manuals, comprehensive trouble shooting guide, spare parts list and written certification, and special bulletins covering on-site storage.

4.	Provide VFD manufacturer’s written certification of technical support and spare parts availability for period specified in Part 2.

5.	Warranty:  VFD manufacturer’s warranty.

6.	Test Reports: Minimum of three (3) copies of field quality control test data.

1.04	QUALITY ASSURANCE

A.	Manufacturer’s Qualifications:  Minimum of five years experience in design and manufacture of VFDs of horsepower, range, and technology specified on Contract Drawings and in this Section.

B.	Manufacturer shall provide quality control laboratory to perform failure analysis.

1.05	WARRANTY

Provide manufacturer’s warranty certificate upon acceptance of VFD system that shall include the following as a minimum:

A.	If defect in supplied apparatus appears, or failure to comply with this Section is identified within period of two (2) years from date of manufacturer’s certified start-up, not to exceed 30 months from shipment, repair VFD within forty-eight (48) hour period.

B.	Contractor shall, without delay and at Contractor’s own expense, correct defects or failure of compliance by repairing defective parts, supplying non-defective replacement parts, or correcting defective or deficient design by any other means recommended by VFD manufacturer and accepted by SDR.

PART 2 - PRODUCTS

2.01	GENERAL

A.	Comply with applicable referenced standards.

B.	Label VFD in compliance with UL 508C.

C.	Provide VFD of fixed direct current (DC) bus type with full-wave input diode bridge.

1.	VFD shall convert three-phase, 60 Hz, input power to three-phase adjustable voltage, adjustable frequency output power using pulse width modulation (PWM) switching techniques.

2.	Base continuous full-load output current rating on 104° F (40° C) ambient, and maximum modulating frequency at which the drive can be programmed.

3.	Submit VFD characteristics output waveforms being supplied to the motor at full speed and full load, assuming VFD is properly sized for motor loads.

4.	Submit typical harmonic current spectrum that will be produced by VFD at full-speed and full-load, assuming the worst case conditions.

D.	Expected Service Life Of Components and Enclosures:  Not less than twenty (20) years with nominal maintenance and repair.

E.	Equipment listed as Altitude Class 1 km per NEMA ICS 1 shall be derated per motor nameplate for altitude indicated in “VFD Environment and Service Conditions” Article.

2.02	VFD SUPPLIED WITH NEW PUMP OR FAN SYSTEM

A.	Pump or fan manufacturer who supplies VFD shall take "unit responsibility" for complete pump or fan, motor, and VFD with all specified components.  Pump or fan is specified in Division 15 specifications and/or in Drawings.

1.	Unit responsibility includes responsibility for interface, and successful operation of system components, that include, but are not limited to, hardware and electronics.

2.	Pump or fan manufacturer is defined as actual manufacturer of variable speed pump or fan.

B.	VFD manufacturer should also be manufacturer of motor.  However, this is not prerequisite for approval.  Submit letter from VFD manufacturer stating that motor nameplate data furnished with system is compatible with VFD, and that system will meet requirements of this Section.

C.	If Contractor provides system other than that specified on Drawings, comply with the following:

1.	Requirements of  Paragraphs A and B above.

2.	Submit harmonic distortion analysis to demonstrate that VFD meets AC harmonic distortion limits.

2.03	VFD SUPPLIED FOR EXISTING PUMP OR FAN SYSTEM

A.	Submit letter from VFD manufacturer stating that use of their VFD is compatible with, and properly sized for existing pump or fan motor nameplate information (provided by SNL), and that it will meet requirements of this Section.  Design engineer shall determine if total system replacement is the appropriate recommendation.

B.	If Contractor proposes substitute for VFD specified on Drawings, in addition to requirements of sections 1600-S, “Materials and Equipment”“Submittals” Article, and 1300-S, “Submittals”, submit harmonic distortion analysis demonstrating that substituted VFD meets AC harmonic distortion limits.

1.	Perform harmonic study analysis in accordance with IEEE 399, Chapter 10 and IEEE 519, Section 8, and account for existing system.

2.	SNL will provide power system data required to perform harmonic analysis study.

2.04	VFD MAXIMUM VOLTAGE AND CURRENT HARMONIC DISTORTION

A.	Perform harmonic study analysis in accordance with IEEE 399, Chapter 10, and IEEE 519, Section 8, and account for existing system parameters.

B.	SNL will provide power system data required to perform harmonic analysis study.

C.	Harmonic Voltage Distortion:  Do not exceed distortion limits at point of common coupling (PCC), as recommended and defined by IEEE 519.

1.	Limit harmonic voltage distortion to 3% of fundamental for individual frequency harmonic.

2.	Limit total harmonic voltage distortion (THVD) to 5% at PCC without major parallel resonance of injected harmonic frequencies .

D.	Harmonic Current Distortion:  Do not exceed distortion limits at PCC as defined in IEEE 519.

2.05	ENCLOSURE

A.	Enclose electrical and electronic components, except for isolation transformer, if required, and remote control devices.

1.	Type 12 enclosure per NEMA 250 and ICS 6, unless noted otherwise on Drawings.

2.	Provide enclosure containing louvers with filters and fans as required for appropriate heat dissipation.

B.	Mount VFD on motor control center (MCC), if indicated in Contract documents.

2.06	Design Feature MINIMUM REQUIREMENTS

A.	Automatic Restart:  Selectable control feature such that upon restoration of input power, VFD will automatically restart and accelerate to speed set by remote speed reference signal.

B.	Speed Controls

1.	Independent minimum speed adjustment, adjustable from 0-100% speed, ± 1%.

2.	Independent maximum speed adjustment, adjustable from 0-100% speed, ± 1%.

3.	Selectable V/Hz adjustment.

4.	Independent acceleration and deceleration adjustments, adjustable over minimum range of 2-120 seconds.

5.	Minimum of three selectable output frequency ranges.

6.	Torque limit regulator, adjustable from 50-100%.

7.	Two selectable stopping modes: Coast and ramp-to-stop.

8.	Bi-directional auto-speed search for starting into rotating loads in both directions and for returning motor to desired speed in proper rotational direction without tripping DC bus .

9.	Upon loss of speed reference signal, VFD shall be selectable/programmable to support customer’s needs and manufacturer’s recommendations, which include the operateion at a preset minimum speed or last best signal in order to prevent interruption to pump or fan system being controlled.

C.	Communications Link and VFD Monitoring and Control Capabilities:  Adjustable speed designed to accept control signal via SNL’s Protocol 1 (P1) network communication connection to Landis and Staefa Series 600 Modular Building Controller (MBC).  Direct communication connection shall be through identical protocol to the Landis and Staefa system, unless otherwise specified in Contract documents.

1.	“Gateway” type protocol translation shall not be accepted.

2.	VFD shall have ability to function on Landis and Staefa System 600 P1 Network as floor level network (FLN) device.

3.	P1 communication driver shall be built into VFD.

4.	At a minimum, VFD control panel shall be able to perform the following tasks via the Landis and Staefa System 600 P1 Network:

a.	Monitor

(1)	Frequency output

(2)	Speed

(3)	Current

(4)	Torque

(5)	Power

(6)	Drive temperature

(7)	kWh

(8)	Run time

(9)	Control variable.

b.	Control:  Provide the following control options.

(1)	Controlled variable may be wired to drive, and control device modulated using control loop built into drive.

(2)	Controlled variable may be wired to drive, and control device modulated using control strategy implemented in Power Process Control Language (PPCL).

(3)	Controlled variable may be wired to system 600 network at remote location.

(4)	Start/Stop

(5)	Speed reference.

D.	DC Bus Discharge Indicator: Incorporate within VFD control system.

E.	Heat Sink Over Temperature Protector:  Incorporate within VFD controller.

F.	VFD Controller:  Provide the following functions (electromechanical or electronic programmable):

1.	Hand-Off-Auto switch with the following features:

a.	"Hand" - fan/pump enabled

b.	"Off"  - fan/pump disabled

c.	"Auto" - remote stop/start enabled

2.	Switch with the following functions:

a.	Position 1 - Manual speed control.

b.	Position 2 - Automatic speed control

3.	Frequently accessed VFD programmable parameters shall be adjustable from digital alpha-numeric keypad located on front door of VFD.  These shall include the control functions specified above.  Programming and messages shall be in the English language and accessible without requiring knowledge of codes.

G.	Provide output load ammeter, voltmeter, and speed indication.

H.	Maximum Acoustical Noise Levels:   For sound originating in VFD equipment, do not exceed 9 decibels above room ambient noise level where equipment will be located.

I.	Efficiency of Total VFD System:  No less than 96.5% at full load when operating at full-speed, and when operating at half-speed, no less than 87% for motors 5 HP or less and  80% for larger motors.

J.	Line Reactors:  Supply and install if required to meet harmonic distortion limits, suitable for VFD application (including any derating factor).  Such reactors may be in separate enclosure from power/control module.

K.	Integrated Withstand Rating:  No less than 25,000 amperes (symmetrical), unless noted otherwise on Contract Drawings.

L.	Capable of power loss ride through to prevent shut-down during power losses for minimum of three cycles.

M.	Input Power Disconnect:  Provide positive disconnecting means between controller and all phases of incoming AC line.

1.	Mount disconnect inside controller enclosure, and include mounting bracket and through-the-door interlocking handle with provisions for padlocking.

2.	Disconnect shall be thermal magnetic, molded case circuit breaker.  Size circuit breaker to interrupt 25,000 amperes (symmetrical) fault current, unless noted otherwise.

N.	Manual Bypass:  Unless otherwise specified on Contract Drawings, provide manual bypass using magnetic contactors.

1.	Provide manufacturer’s written certification stating that integrated withstand rating of VFD is no less than 25,000 amperes (symmetrical), unless noted otherwise in Contract documents.

2.	Include circuitry necessary to safely transfer motor from VFD to power line, or from power line to VFD while motor is at zero speed.

3.	Utilize two motor contactors, electrically and mechanically interlocked.  Use NEMA-rated contactors;  do not use IEC-type contactors.  One contactor is connected between controller output and motor, and is controlled by controller regulator. Second contactor is connected between bypass power line and motor, providing across-the-line starting.

4.	Provide motor protection in both "controller" mode and "bypass" mode by motor overload relay.  Relay control logic shall be 120 volts AC.

a.	Include common start-stop commands in "controller" mode and "bypass" mode within this enclosure.

b.	Bypass circuit shall include door interlock, main power input disconnect circuit breaker that provides positive shutdown of input power to both bypass circuitry and VFD.

5.	Bypass circuit shall provide ability to safely troubleshoot and test VFD controller, both energized and de-energized, while operating in "bypass" mode.

6.	Mount equipment within VFD controller enclosure.

O.	Provide panel-mounted diagnostic module that includes functions listed in “Diagnostic Fault Indicators” Article.  VFD unit-mounted alpha-numeric keypad which performs specified diagnostic functions is acceptable.

P.	Operation of VFD at full-load will have aminimum of 95 percent or greater lagging displacement power factor.

2.07	Protective Features

A.	VFD shall be designed to be self-protecting from electrical  damage due to normal transients and surges in incoming power line, grounding or disconnection of its output power, and interruption in or runaway of incoming speed reference signal.

1.	Protection is defined as normal shutdown with no component damage.

2.	Available Fault Current at VFD:  25,000 amperes, unless noted otherwise.

B.	Include the following protective features:

1.	Ground fault protection.

2.	Short circuit protection.

3.	Overload protection of VFD unit.

4.	Separate motor overload relay with reset button extending through door.

5.	Minimum current limit adjustable (output of drive) from 60-100%.

6.	Current limited stall prevention.

7.	Current limiting DC bus fuse, or electronic DC bus protection.

8.	DC bus under voltage.

9.	DC bus over voltage.

10.	Loss of input phase protection.

11.	Over frequency protection.

12.	Over temperature protection.

13.	Motor over temperature protection.

14.	Stator winding overcurrent protection.

15.	Open phase or missing gate protection.

16.	Gate power supply loss protection.

17.	Instantaneous electronic overcurrent trip for transistorSCR protection.

2.08	Diagnostic Fault Indicators

A.	VFD shall include continuous self-diagnostics for fault conditions.  Faults shall be displayed on front panel.

B.	Faults displayed by diagnostic module shall include:

1.	Overcurrent.

2.	Short circuit.

3.	Ground fault.

4.	Overload.

5.	Over voltage.

6.	Under voltage.

7.	Over temperature.

8.	Control function error.

2.09	VFD Environmental and Service Conditions

VFD system shall be designed to operate within the following environmental or service conditions:

A.	Ambient Service Temperature:  0°C to 40°C.

B.	Humidity:  Non-condensing to 90%.

C.	Altitude:  5,500 feet (1.7 km).

D.	Input Voltage: 200 volts AC ± 10% or 460 volts AC ± 10%, as specified in Contract documents.

E.	Input Frequency:  60 hertz ± 2%.

F.	Other potential environmental detriments which may include excessive dust or vibration.

2.10	VFD Motor Requirements

A.	New pump or fan motors operated from VFD system shall meet the following requirements:

1.	Constructed and applied per NEMA MG 2.

2.	Continuous-Duty Operation:  NEMA MG 1 Design B, specifically Part 31.40.4.2

3.	Service Factor:  1.15.

4.	Insulation:   Class F

5.	Energy Efficiency:  Comply with NEMA MG 10 and 10 CFR 435.106, and determine efficiency using IEEE 112, Test Method B.

6.	Classification:  Inverter Duty

B.	For existing or separately supplied pump or fan motors to be operated from VFD system,  coordinate nameplate information and/or refer to Contract documents.  Refer to “VFD Supplied for Existing Pump or Fan System” Article for requirements.

2.11	SOURCE QUALITY CONTROL

Testing:  Printed circuit boards shall be completely tested and burned in before assembly into VFD.  VFD shall then be subjected to preliminary test for minimum of four hours.

A.	Perform test at 104°F (40° C) ambient, full rated load, or cycled load.

B.	Continuously cycle drive input power for maximum stress and thermal variation.

C.	Provide comprehensive trouble shooting guide, and phone number for maintenance and operation questions to be answered.

2.12	Spare Parts/technical support

A.	Identify critical spare parts and long lead time delivery items that should be recommended for SNL in-house stock.

B.	Provide spare parts as recommended by VFD manufacturer, unless otherwise specified in Contract documents.  Spare parts should include the following minimum:

1.	One set of fuses for each fuse size.

2.	One power transistor for each transistor rating supplied.

C.	Provide written certification from VFD supplier that spare printed circuit boards of each type utilized in VFD are readily available to SNL from VFD manufacturer within 24 hours of order.  Describe each part and/or module and list stock number(s) of such parts.

D.	Provide written certification from VFD manufacturer stating the availability of technical support, and spare parts for minimum of five (5) years from start-up.

E.	Provide technical support on the following basis:

1.	Respond within 4 hours for diagnosis of  the problem.

2.	Respond within 24 to 36 hours to repair the problem.

2.13	TEST AND INSPECTION EQUIPMENT

A.	Manufacturer shall inform SNL through their bid submittal, if VFD or VFD system provided requires any special tool or equipment to test, analyze or maintain system, and include additional price list for said equipment

B.	At SNL’s option, manufacturer may be required to furnish said tool or equipment, if Paragraph A above is applicable.

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Examine areas and conditions under which VFD system is to be installed, and provide SDR with written notification of conditions detrimental to proper completion of Work.

B.	Do not proceed until unsatisfactory conditions have been corrected in manner acceptable to SDR.

3.02	PREPARATION

Provide indoor storage for VFD to meet service conditions requirements of Part 2.

3.03	INSTALLATION

A.	Comply with Contract documents, and requirements as referenced herein.

B.	Comply with manufacturer's written installation instructions, and requirements of Division 16, Section “Electrical Work.”

C.	In case of conflict, follow the most stringent requirement and contact SDR for concurrence.

D.	Install warning label on VFD, AHU, pump, etc. indicating that load is subject to automatic restart upon restoration of power.

3.04	Field QUALITY CONTROL

A.	Notify SDR minimum of two weeks prior to scheduled test, checkout, and start-up.

B.	Do not energize any portion of VFD system without authorization from VFD manufacturer's representative and SDR.

C.	Provide visual inspection of VFD prior to start-up, and document the following:

1.	Presence of moisture or debris inside equipment.

2.	Damage or dents to VFD enclosure.

3.	Damaged, disconnected, or loose components, conductors or terminal connectors.

4.	Possible restrictions to air flow at VFD cooling fans or heat sink.

5.	Unremoved shipping blocks or tapes at power contactors, relays, etc.

D.	Correct deficiencies found during visual inspection prior to commencing start-up of VFD, and provide written documentation.

E.	Demonstrate trouble-free, stable operation for following conditions:  starting, full load, three-quarter load, half load, one-quarter load, no load, and intermediate loads.

F.	SNL will test VFD with Dranetz Model 658 power analyzer at point of common coupling, at no charge to Contractor, before and after installation.  Power analyzer is capable of measuring total harmonic voltage and current distortion for all planned operating speeds of the VFD system..

If harmonic voltage and current distortion exceed limits specified in Part 2, Contractor shall furnish and install, at no cost to SNL, devices necessary to reduce distortion to acceptable limits.

G.	VFD manufacturer's service engineer shall prepare final written documents of installation and inspection tests made in field, complete with meter readings and recordings, where applicable, and submit to SDR for approval.  Data collected from these tests shall include:

1.	Incoming voltages from each phase leg to neutral, and from phase to phase.

2.	External process signal and its source.

3.	Set-Up Parameters:  Comply with SNL’s written instructions.

a.	Acceleration time to full motor speed in seconds.

b.	Deceleration time from full motor speed in seconds.

c.	Second acceleration/deceleration as applicable.

d.	Maximum speed in hertz and RPM.

e.	Minimum speed in hertz and RPM.

4.	Operational Parameters

a.	Line current for each phase at inverter at one-quarter load, half load, three-quarter load, and full load.

b.	Line current for each phase at bypass in bypass mode.

c.	Load current for each phase at inverter at one-quarter load, half load, three-quarter load, and full load.

d.	Load current for each phase at bypass in bypass mode.

5.	Ambient temperature during test.

6.	DC bus voltage.

7.	Frequency output at 100% reference signal.

8.	Name of person completing test and start-up procedure.

9.	Date start-up completed.

END OF SECTION