SPILL PREVENTION, CONTROL, AND COUNTERMEASURES PLAN

NATIONAL WEATHER SERVICE

St. Louis Weather Forecast Office

12 Missouri Research Park Drive

St. Charles, Missouri 63304

Original Date of Plan	:	February 19, 1993

Date of Last Plan Review	:	March 19, 2002

Date of Last Amendment

and P.E. Certification	:	March 19, 2002

Designated Person Responsible for Spill Prevention:

Neil Hill, Environmental Focal Point

Telephone: (636) 447-1876

CERTIFICATION

I hereby certify that I have examined the facility, and being familiar with the provisions of Title 40 of the Code of Federal Regulations Part 112, I attest that this Spill Prevention, Control, and Countermeasures (SPCC) Plan has been prepared in accordance with good engineering practices.

| John McCall |
| --- |
| Printed Name of Registered Engineer |
| Signature of Registered Engineer and Date |
| Registration No. PE-050653-E | State PA |

REVIEW DOCUMENTATION AND MANAGEMENT APPROVAL PAGE

REVIEW DOCUMENTATION

In accordance with Title 40 of the Code of Federal Regulations (CFR) Part 112.5(b), a review and evaluation of this Spill Prevention, Control, and Countermeasures (SPCC) Plan is conducted at least once every 3 years.  As a result of this review and evaluation, the National Weather Service will amend the SPCC Plan within 6 months of the review to include more effective prevention and control technology if:

C	Such technology will significantly reduce the likelihood of a spill event from the facility, and

C	If such technology has been field-proven at the time of review.

Any amendment to the SPCC Plan shall be certified by a Professional Engineer within 6 months after a change in the facility design, construction, operation, or maintenance occurs that materially affects the facility’s potential for the discharge of oil into or upon the navigable waters of the United States or adjoining shorelines.

| Review Date | Signature of Responsible Manager | Amended (Yes or No)? 1 |
| --- | --- | --- |

1	Amendment necessary and certified by a Registered Professional Engineer per Title 40 CFR Part 112.3(d)

MANAGEMENT APPROVAL

The National Weather Service is committed to the prevention of discharges of oil to navigable waters and the environment.  We maintain the highest standards for spill prevention, control, and countermeasures through regular review, updating, and implementation of this SPCC Plan for the Weather Forecast Office.

Steve Thomas, Meteorologist in Charge

Printed Name and Title of Responsible Manager

Signature and Date

CONTENTS

Section	Page

Certification	i

Review Documentation and Management Approval	ii

PART I - GENERAL INFORMATION	1

A.	GENERAL	1

1.	Name	1

2.	Type	1

3.	Date of Initial Operation	1

4.	Location	1

5.	Name and Address of Operator	1

6.	Facility Contacts	1

B.	SITE DESCRIPTION AND OPERATIONS	1

1.	Facility Location, Layout, and Operations	1

2.	Facility Storage	2

3.	Drainage Pathway and Distance to Navigable Waters	2

4.	Spill History	2

5.	Spill Potential, Volumes, and Rates	2

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES FOR SPILL PREVENTION AND CONTROL	4

A.	SPILL PREVENTION	4

1.	Bulk Storage Tanks and Facility Transfer Operations	4

2.	Tank Truck Unloading Operations	4

3.	Inspections and Records	5

4.	Site Security	5

5.	Training	6

B.	SPILL CONTROL	6

1.	Secondary Containment Designs, Construction Material, and Volume	6

2.	Spill Kits Type and Location	6

PART III - SPILL COUNTERMEASURES AND REPORTING	7

A.	SPILL COUNTERMEASURES	7

B.	SPILL REPORTING	8

1.	General Notification Procedures for All Spills	8

2.	Federal Notifications	8

3.	State Notification	9

4.	Cleanup Contractor Notification	9

PART IV - RECOMMENDED IMPROVEMENTS	10

A.	PHYSICAL UPGRADES	10

1.	Containment	10

2.	Spill Kits	10

B.	PROCEDURAL CHANGES	10

1.	Inspections and Preventative Maintenance	10

2.	Training	10

Appendix

A	TANK ULLAGE/FUELING LOG AND FUEL UNLOADING PROCEDURE CHECKLIST

B	INSPECTION CHECKLISTS

C	TRAINING OUTLINE AND TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, SECTION 112.1-112.20-OIL POLLUTION PREVENTION

D	SPILL REPORTING FORM

E	CROSS REFERENCE OF THE REQUIREMENTS of TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, Section 112.7, WITH THIS PLAN

FIGURES

Figure	Page

1	SITE LOCATION	11

2	SITE LAYOUT	12

TABLES

Table	Page

1	DESCRIPTIVE INVENTORY OF FACILITY STORAGE	13

2	POTENTIAL SPILL SOURCES AND VOLUMES	14

PART I - GENERAL INFORMATION

- GENERAL

This section provides general information about the facility.

  - Name

National Weather Service (NWS)

St. Louis Weather Forecast Office (WFO)

  - Type

This facility is an onshore facility (non-production) that operates as a weather forecast center and is staffed 24 hours per day, 7 days per week, and 365 days per year.

  - Date of Initial Operation

September 1990

  - Location

12 Missouri Research Park Drive

St. Charles, St. Charles County, Missouri 63304

  - Name and Address of Operator

National Weather Service

12 Missouri Research Park Drive

St. Charles, Missouri 63304

  - Facility Contacts

Name	Title	Telephone Number

Neil Hill 	Environmental Focal Point	(636) 447-1876 Ext. 4455

Steve Thomas	Meteorologist in Charge	(636) 447-1876

- SITE DESCRIPTION AND OPERATIONS

This section describes the site location, its operations that store diesel fuel, site drainage patterns, spill history, and spill potential.

  - Facility Location, Layout, and Operations

The facility is located in St. Charles County, Missouri, approximately 1.5 miles northwest of the Missouri River (Figure 1).  Figure 2 shows the layout of the facility.  Fuel used by the facility is stored in a 775-gallon aboveground storage tank (AST) that provides fuel to the WFO emergency backup generator.  A 10-gallon, heated day tank is associated with that generator, and the day tank and generator are located in an enclosed generator shed approximately 15 feet east of the main operations building.  Two 225-gallon tanks that store fuel for the Radar Data Acquisition (RDA) unit also are located at the facility.  Both tanks are located in the RDA generator shed and are connected by a fuel line.

Estimated fuel usage at the facility is 1,000 gallons per year for both generators, which are tested automatically each week.  WFO generator testing occurs for approximately 1 hour per week, and RDA generator testing occurs for approximately 0.5 hour per week.  Fuel consumption would increase based any power outages caused by severe weather in the area.

  - Facility Storage

The 775-gallon AST is cylindrical in shape, situated horizontally, and is constructed of welded steel plates in conformance with Underwriter Laboratories specification 142 (UL 142).  A 2-foot-high concrete dike provides the tank with secondary containment.  The diked storage area is equipped with a manually operated drainage valve that normally is closed.  However, when rainwater enters the storage area, it is inspected for a sheen before the valve is opened to release the collected water.

The 775-gallon AST supplies fuel to the 10-gallon day tank through 0.75-inch iron piping contained in 4-inch polyvinyl chloride piping.  The day tank is a rectangular, single-wall, steel tank that is set in an open-top spill pan (rupture basin).  The day tank is connected to the generator by flexible rubber supply and return lines.

The two 225-gallon RDA tanks are rectangular and are constructed of welded steel plates.  Both tanks are collocated with the RDA generator in a concrete generator shed that provides secondary containment for the tanks.

Table 1 summarizes the pertinent information on the tank at the facility.

  - Drainage Pathway and Distance to Navigable Waters

If fuel spills during fuel unloading for the 775-gallon AST, it would travel along the parking lot to a storm drain approximately 60 feet southeast of the AST.  Fuel spilled from the area of the RDA tanks would travel north approximately 40 feet to the previously referenced storm drain.  The storm drain discharges into a drainage culvert approximately 500 feet northeast of the AST (Figure 2).

  - Spill History

Reportable spill events from start of operations (September 1990) to present (date on cover of this plan):   None.

  - Spill Potential, Volumes, and Rates

The most probable causes of spills from the tanks are from overfilling, a ruptured hose during fuel unloading, or failure of the fuel supply line to the day tank.  Spills caused by loss of structural integrity, vehicle collision, or natural disaster are low probability events.  For the day tank, the probable causes of spills are from failure of the pump to shut down or failure of the line from the pump to the day tank.

Table 2 summarizes the potential type of failure, potential spill volume, estimated rate, and direction of spill flow from the tanks.

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES 
FOR SPILL PREVENTION AND CONTROL

This section discusses spill prevention and control measures that shall be implemented at the facility.

- SPILL PREVENTION

This section describes design components and operating procedures that shall be implemented at the facility to prevent oil spills.

  - Bulk Storage Tanks and Facility Transfer Operations

AST and RDA tanks:  Construction of the AST and RDA tanks is compatible with the No. 2 diesel fuel stored in the tanks.  The 775-gallon AST is located inside a 2-foot-high, concrete, secondary containment dike.  The RDA generator shed provides adequate secondary containment for the RDA tanks.  For all three tanks, automatic shut-off valves on the fill spouts are set to close when each tank reaches 90 percent of full capacity.

Day Tank:  The day tank is located inside a building that provides sufficient containment for the tank contents.  It also is equipped with an open top spill pan (rupture basin) designed to hold the entire tank volume.

Piping:  An antisiphoning valve is located between the 775-gallon AST and the pump to prevent unwanted fuel from being siphoned from the storage tank.  The aboveground piping from the AST to the day tank pump is equipped with a polyvinyl chloride pipe sleeve to protect it from corrosion.

  - Tank Truck Unloading Operations

All delivery drivers have received U.S. Department of Transportation hazardous material transportation training, as required by Federal law.

The remainder of this section discusses the procedures that shall be used during unloading of fuel from the tank truck into the storage tank to prevent spills.  This procedure shall be documented every time refueling occurs in the form found in Appendix A.  Copies of this form shall be kept for 3 years.

The following procedure is used prior to fuel unloading:

•	Move spill containment equipment, such as booms or spill barriers, into the unloading area.

•	Ensure that the audible high-level alarm system and the automatic shutoff valve are functioning properly.

•	Determine the available capacity (ullage) of the tank by converting the reading on the fuel gauge to gallons (see Appendix A).  This ullage is communicated to the fuel supply contractor and marked in the fueling log.

•	Block the tank truck wheels.

•	Place drip pans under all pump hose fittings (if applicable) prior to unloading.

•	Ensure the fill nozzle is placed in the appropriate tank appurtenance.

Both the NWS representative and the delivery driver shall remain with the vehicle at all times during unloading.  Gauges on the tank and the truck shall be continuously monitored to ensure the ullage is not exceeded.  If either the audible or visual alarms engage, the unloading of fuel shall be stopped as soon as possible.

After fuel unloading is completed:

•	Record the amount of fuel transferred to the tank in the log (Appendix A).

•	Drain the fill hose and then ensure that all drain valves are closed (if applicable) prior to removal of the hose from the tank.

•	Pour any fuel in the drip pans, tank truck containment pool, or spill container on the fill pipe into the tank (if it has the capacity), or dispose of it appropriately.

•	Inspect the tank truck prior to removing the blocks to ensure the lines have been disconnected from the tank.

•	Remove the blocks from the truck wheels.

•	Place a copy of the fuel unloading checklist in the SPCC plan.

  - Inspections and Records

Inspection and Maintenance of Tanks:  The AST, RDA tanks, and day tank shall be inspected weekly for any oil outside the tanks, especially at seams (including the underside).  The concrete dike shall be inspected for cracks.  The outside of exposed piping also shall be inspected weekly, especially at the joints such as gasket fittings.  Monthly and annual inspections shall follow the checklists shown in Appendix B.

Record Keeping:  The Environmental Focal Point or designated alternate is responsible for completing the ullage logs and documenting fuel unloading procedures.  These records, as well as records of all inspections, shall be maintained for at least 3 years from the time of inspection.

  - Site Security

The facility is equipped with adequate lighting in the two fuel storage areas.  Personnel are on site and monitor an external video surveillance system continuously.  The WFO and RDA generator sheds are kept locked.  Signage around the tanks warns of the presence of a combustible liquid, that the combustible liquid is No. 2 diesel fuel, and that smoking is not permitted near the tanks.  Fire extinguishers are located near the WFO and RDA generators.  The tanks are not located in the direct line of parking lot traffic; therefore, no guard posts are required.

  - Training

The Environmental Focal Point (person responsible for spill prevention) and an alternate shall be trained in the intent of applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in paragraph 3, above.  Spill control and countermeasures also shall be included in the training.

Training shall be repeated once per year.  All new personnel responsible for implementing this SPCC plan shall be properly trained before beginning the new position.  A record of who was trained, when, and by whom, shall be filed with this SPCC plan and kept for a period of 3 years.

- SPILL CONTROL

This section describes control measures that shall be implemented to prevent any spilled oil from entering navigable waters or adjoining shorelines.

  - Secondary Containment Designs, Construction Material, and Volume

The 775-gallon AST is located inside a concrete secondary containment dike that completely encloses the AST and is designed to prevent any spill from leaking beyond the diked area.

The day tank and two RDA tanks are located inside buildings that provide adequate containment and protection from the elements.  In addition, the day tank is equipped with a rupture basin that would prevent any release from reaching the floor of the WFO generator building.

  - Spill Kits Type and Location

The facility shall have kits designed to absorb diesel fuel and which can prevent discharged oil from reaching nearby water bodies or storm sewers.  The kits include oil absorbent socks and mats in a polyethylene container can be used as a disposal container.  These items are stored in the generator sheds.

PART III - SPILL COUNTERMEASURES AND REPORTING

The primary emphasis of this SPCC plan is on prevention.  The spill countermeasures presented do not constitute a contingency plan detailed in Title 40 CFR Part 109, nor is one required.  Such a plan is only required under Title 40 CFR 112.7(d) if it is impracticable to provide containment, diversionary structures, or equipment to prevent the discharge of oil to navigable waters.  In addition, this facility is not required to have a facility response plan under Title 40 CFR Part 112.20 because it does not:

C	Transfer oil over water from vessels and have a total oil storage capacity of greater than or equal to 42,000 gallons, or

C	Have a total storage capacity over 1 million gallons.

- SPILL COUNTERMEASURES

This section presents countermeasures to contain, clean up, and mitigate the effects of an oil spill that impacts navigable waters or adjacent shorelines.

A spill containment and cleanup activity will never take precedence over the safety of personnel.  No countermeasure activities will be undertaken until conditions are safe for workers.  The “SWIMS” procedure should be implemented as countermeasures:

S   -	Stop the leak and eliminate ignition sources.

a. 	Attempt to seal or some how stop leak if it can be done safely.

b. 	Attempt to divert flow away from catch basins with a spill barrier or the contents of the spill kit.

c. 	Eliminate all ignition sources in the immediate area.

W  -	Warn others.

a.  	Yell out “SPILL.”  Inform the person in-charge at your facility.

b. 	Account for all personnel and ensure their safety.

c. 	Notify contacts and emergency response contractor as described in the following section for assistance in control and cleanup.

I    -	Isolate the area.

a. 	Rope off the area.

M  -	Minimize your exposure.  Stay upwind.

S    -	Stand by to assist the emergency response contractor, if necessary.

- SPILL REPORTING

This section discusses the reporting procedures for spills of diesel fuel at the facility.  The individuals and organizations that are notified vary based on the quantity of the spill, whether it reaches navigable waters or adjoining shorelines, and the frequency of spills.

A spill report form that requests the information to be reported to all agencies in written form (to the extent known) is included in Appendix D.  Copies of the completed form should be submitted, preferably by e-mail, to the NWS Environmental Compliance Officer and the NOAA Regional Compliance Officer.

  - General Notification Procedures for All Spills

The responsible person or designee is directly charged with reporting all oil spills that result from facility operations as follows:

•	First, call 9-1-1 (or the local emergency agency) if there is an immediate emergency

•	Next, notify the appropriate individuals within the NWS:

1.		Mike Jacob, (301) 713-1838 Ext. 165, JMichael.Jacob@noaa.gov, NWS Environmental Compliance Officer

2.		Olga Kebis, (301) 713-1838 Ext. 173, Olga.Kebis@noaa.gov, NWS Safety Officer

3.		Kirt Grahl, (816) 426-3226, Ext. 470, Kirt.Grahl@noaa.gov, NWS Central Regional Environmental/Safety Coordinator

4.		Sherilyn Villegas, (816) 426-3925, Ext. 263, Sherilyn.S.Villegas@noaa.gov, NOAA Central Regional Compliance Officer

  - Federal Notifications

The Federal Clean Water Act as described in Title 40 CFR Part 110.6, requires notifying the U.S. Environmental Protection Agency’s (EPA) National Response Center (or the U.S. Coast Guard [USCG]) as soon as anyone has knowledge of any discharges of oil in quantities that “may be harmful.”  Title 40 CFR Part 110.3 defines “may be harmful” as a discharge that:

•	Violates applicable water quality standards, or

•	Causes a film or sheen upon or discoloration of the surface of the water or adjoining shorelines or causes a sludge or emulsion to be deposited beneath the surface of the water or upon adjoining shorelines.

If either of these criteria are met contact:

•	The National Response Center (EPA and USCG):  (800) 424-8802

Under the SPCC regulations, spill information listed in Title 40 CFR Part 112.4(a) must be reported to the regional EPA office within 60 days if either of the following occurs:

•	A discharge of more than 1,000 gallons of oil into or upon navigable waters or adjoining shore lines in a single event, or

•	Two spill events that cause visible sheens upon navigable waters or adjoining shore lines within any 12-month period.

Diesel fuel is not listed as a hazardous substance under the Comprehensive Environmental Response, Compensation, and Liability Act (CERCLA); therefore, no other notification to the EPA is required for discharges of diesel fuel other than those listed above.

  - State Notification

To satisfy the state reporting requirements, the location and quantity of any spill must be determined.  Under the Missouri Revised Statute Chapter 260, Section 500, a reportable quantity (RQ) is defined as follows:

•	If spilled on the surface of the land, any quantity of oil over 50 gallons, or

•	If spilled into the waters of the state, any quantity that would produce a visible oil slick, oil solids, or coat aquatic life, habitat, or property with oil.

If one or both of these criteria are met, contact:

•	Missouri Emergency Response Commission (24 hours): (573) 634-2436

  - Cleanup Contractor Notification

An emergency response contractor should be notified to assist with the clean up, if necessary.  Contact information for at least three contractors shall be maintained in this plan.  NWS has identified the following contractors that are available for emergency response:

•	Odesco Industrial Services 		(618) 254-4874 or (800) 423-1954

•	Riedel Environmental Services, Inc.	(636) 970-6569

•	Environmental Specialists, Inc.		(816) 523-5081

•	Safety Kleen				(636) 441-0104

PART IV - RECOMMENDED IMPROVEMENTS

In accordance with Title 40 CFR Part 112.7, this section presents physical upgrades or procedural changes that are not yet fully operational but are called for in the plan.

- PHYSICAL UPGRADES

  - Containment

A float switch designed to detect fuel that has leaked or been spilled from the day tank should be installed.  A float switch would automatically shut off the pump and should be connected to the audible alarm system.  This upgrade should be implemented within 6 months of the date of this plan.

  - Spill Kits

The facility shall maintain sufficient spill kit materials such as absorbent pads and mats sufficient to prevent a spill from reaching a nearby water body or storm sewer.  Because there is a storm drain located in close proximity to each of the tanks at the site, urethane spill barriers or similar devices are recommended that may be more effective than the absorbent materials alone.  Urethane spill barriers are not a mandatory requirement so long as a sufficient amount of absorbent materials or other equipment/supplies are maintained that can prevent fuel from reaching a storm drain in the event of a spill.

- PROCEDURAL CHANGES

  - Inspections and Preventative Maintenance

The inspection checklists found in Appendix B should be followed.  This requirement is found in 40 CFR Part 112.7(e)(8).  Visual inspections include observing for any signs of cracking in the concrete secondary containment unit for the 775-gallon AST or for signs of corrosion on the steel tanks.

  - Training

The Environmental Focal Point (person responsible for spill prevention at the facility) and an alternate should be trained in the intent of the applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in the previous section.  Spill control and countermeasures also should be included in the training.  The alternate should be designated in case the primary person is off the site at the time of a spill.  A recommended outline for the training is found in Appendix C.

Training should be repeated once per year.  All new personnel responsible for implementing the SPCC plan should be properly trained before beginning the new position.  A record of who was trained, when, and by whom should be filed with this SPCC plan and kept for a period of 3 years.  This requirement is found in Title 40 CFR 112.7(e)(10).

Spill prevention briefings for operating personnel should be conducted at frequent intervals to ensure adequate understanding of the SPCC plan and to describe spill events or failures, malfunctioning components, and recently developed precautionary measures.

Figure 1 Site Location

Figure 2 Site Layout

TABLE 1

DESCRIPTIVE INVENTORY OF FACILITY STORAGE

| Tank | Nominal Capacity (Gallons) | Product Stored | Type | Double Walled? |
| --- | --- | --- | --- | --- |
| WFO Generator AST | 775 | No. 2 diesel fuel | AST | No |
| WFO Generator Day Tank | 10 | No. 2 diesel fuel | AST | No |
| RDA Generator AST | 225 | No. 2 diesel fuel | AST | No |
| RDA Generator AST | 225 | No. 2 diesel fuel | AST | No |
| Total Capacity | 1,235 |  |  |  |

Note:	AST	Aboveground storage tank

TABLE 2

POTENTIAL SPILL SOURCES AND VOLUMES

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| 775-gallon WFO AST | Overfilling or a ruptured hose during fueling | >0 to 20a | 40b | Southeast | None. |
|  | Failure of fuel supply line to pump | >0 to 775 | Variable | Southeast | Can be minimized through routine inspections. |
|  | Structural failure or vandalism | >0 to 775 | Variable | Southeast | Low probability that AST and secondary containment would fail. |
|  | Vehicle collision | >0 to 775 | Variable | Southeast | Low probability that AST and secondary containment would fail. In addition, vehicle traffic is limited, and traffic flow is not directly toward AST. |
|  | Overturn or puncture during natural disaster | >0 to 775 | Variable | Southeast | Low probability that AST and secondary containment would fail. |
| Generator Day Tank | Failure of the pump to shut down after filling day tank or failure of the line from pump to day tank. | >0 to 775 | Variable | Southeast | Can be minimized through routine inspections. |
|  | Failure of fuel return line | >0 to 10 | 10c | Southeast | Can be minimized through routine inspections. |
|  | Structural failure or vandalism | >0 to 10 | Variable | Southeast | Low probability event can be minimized through regular inspections and maintenance. |
|  | Overturn or puncture during natural disaster | >0 to 10 | Variable | Southeast | Low probability event. |

Notes:

a	Based on a maximum pumping rate of 40 gallons per minute from the fill truck and a maximum of 30 seconds to turn off the pump.

b	Approximate maximum pumping rate of fill truck.

c	Estimated return line flow rate.

TABLE 2

POTENTIAL SPILL SOURCES AND VOLUMES

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| 225-gallon RDA Tanks | Overfilling or a ruptured hose during fueling | >0 to 20a | 40b | North | None. |
|  | Failure of fuel supply line to pump | >0 to 225 | Variable | North | Can be minimized through routine inspections. |
|  | Structural failure or vandalism | >0 to 225 | Variable | North | Low probability event can be minimized routine inspections and maintenance. |
|  | Overturn or puncture during natural disaster | >0 to 225 | Variable | North | Low probability event. |

Notes:

a	Based on a maximum pumping rate of 25 gallons per minute from the fill truck and a maximum of 30 seconds to turn off the pump.

b	Approximate maximum pumping rate of fill truck.

c	Estimated return line flow rate.

APPENDIX A

TANK ULLAGE/FUELING LOG AND

FUEL UNLOADING PROCEDURE CHECKLIST

(2 Pages)

APPENDIX A-1

TANK ULLAGE AND FUELING LOG

Tank Capacity 			  gallons

| Date | Initials | Gauge Reading | Initial Volume of Fuel in Tanka (Gallons) | Available Capacity or Ullageb (Gallons) | Quantity Added (Gallons) | Comments |
| --- | --- | --- | --- | --- | --- | --- |

Note:

a	From gauge reading

b	Available capacity = tank capacity - initial volume of fuel in tank

APPENDIX A-2

FUEL UNLOADING PROCEDURE CHECKLIST

Date:										Tank:

NWS Representative:								Supplier:

| / | ITEM | DESCRIPTION | COMMENT |
| --- | --- | --- | --- |
| The following six items must be completed prior to fuel unloading: |
|  | 1 | Move spill containment equipment, such as booms or spill barriers, into the unloading area. |  |
|  | 2 | Ensure the audible high-level alarm system and automatic shutoff valve are functioning properly. |  |
|  | 3 | Determine the available capacity (ullage) of the tank by converting the reading on the fuel gauge to gallons (see Appendix A, Page A-1 in SPCC plan). This ullage should then be marked in the fueling log and communicated to the tank truck-unloading contractor. |  |
|  | 4 | Block the wheels of the tank truck. |  |
|  | 5 | Drip pans should be placed under all pump hose fittings (if applicable) after the hose is hooked up to the tank and prior to unloading. |  |
|  | 6 | Ensure the fill nozzle is placed in th appropriate tank appurtenance. |  |
| During unloading |
|  | 7 | Ensure that the NWS representative and the tank truck operator remain with the vehicle at all times during unloading. |  |
|  | 8 | Monitor the gauges on the tank and the truck continuously to ensure the ullage is not exceeded. If the audible high-level alarm sounds, the unloading of fuel is stopped as soon as possible. |  |
| After fuel unloading is completed |
|  | 9 | Record the amount of fuel unloaded in the log (Appendix A, Page A-1). |  |
|  | 10 | Prior to removing the fill hose from the tank, ensure that it is drained and that all drain valves are closed (if applicable). |  |
|  | 11 | Any fuel in the drip pans or spill container on the fill pipe should be poured into the tank (if it has the capacity) or disposed of appropriately (describe how it was disposed of, if applicable). |  |
|  | 12 | Inspect the tank truck prior to removing the blocks to ensure the lines have been disconnected from the tank. |  |
|  | 13 | Remove the blocks from tank truck wheels. |  |
|  | 14 | Return the catch basin outlet valve in the adjacent parking lot to the “open” position. |  |
|  | 15 | Place a copy of this fuel-unloading checklist in the SPCC plan. |  |

APPENDIX B

INSPECTION CHECKLISTS

(3 Pages)

APPENDIX B

INSPECTION FORMS

| MONTHLY INSPECTION CHECKLIST (Page 1 of 2) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| TANKS | YES | NO | NOTES |
| 1. Are there any oil stains on the outside of the tank, including the underside? |  |  |  |
| 2. Is there any oil on the ground, concrete, or asphalt around the tank? |  |  |  |
| 3. Are there any visible cracks or indications of corrosion on the tank, at fittings, joints, or seals (such as paint peeling or rust spots)? |  |  |  |
| 4. Are there any raised spots, dents, or cracks on the tank? |  |  |  |
| 5. Does it appear that the foundation has shifted or settled? |  |  |  |
| 6. Is the fuel gauge working properly? |  |  |  |
| 7. Are all vents clear so they may properly operate? |  |  |  |
| 8. If rainwater is present in secondary containment area, does sufficient capacity remain for spill control? (If applicable) |  |  |  |

| MONTHLY INSPECTION CHECKLIST (Page 2 of 2) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| B. PIPING | YES | NO | NOTES |
| 1. Is there any oil on the outside of or under any aboveground piping, hoses, fittings, or valves? |  |  |  |
| 2. Are aboveground piping, hoses, fittings, or valves in good working condition? |  |  |  |
| C. SECURITY/SAFETY/SPILL COUNTERMEASURES |  |  |  |
| 1. Are lights working properly to detect a spill at night? |  |  |  |
| 2. Are all locks in the “lock” position? |  |  |  |
| 3. Are all warning signs properly posted and readable? |  |  |  |
| 4. Are vehicle guard posts in place and properly secured (if applicable)? |  |  |  |
| 5. Are spill kits easily accessible, protected from the weather, and complete? |  |  |  |
| Corrective Actions Required: |  |  |  |

| ANNUAL INSPECTION CHECKLIST (Page 1 of 1) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| A. MONTHLY CHECKLIST | YES | NO | NOTES |
| 1. Have monthly inspection checklists been completed? |  |  |  |
| B. TANKS |  |  |  |
| 1. Are all alarms and automatic shutoff devices working properly? |  |  |  |
| 2. Is interstitial monitor functioning properly (if applicable)? |  |  |  |
| C. OTHER |  |  |  |
| 1. |  |  |  |
| Corrective Actions Required: |  |  |  |

APPENDIX C

TRAINING OUTLINE AND TITLE 40 OF THE CODE OF FEDERAL REGULATIONS SECTION 112.1 THROUGH 112.20 - OIL POLLUTION PREVENTION

(29 Pages)

APPENDIX C

OUTLINE FOR SPILL PREVENTION, CONTROL, AND COUNTERMEASURES TRAINING

Training will be provided for facility personnel at the following times:

C	System startup or whenever new equipment is installed

C	Within the first week of employment for new personnel

C	Annually

The training will include complete instruction in the elements of the facility’s Spill Prevention, Control, and Countermeasures Plan and will include the following:

A.	Pollution Control Laws, Rules, and Regulations Including a Summary of Title 40 of the Code of Federal Regulations Part 112, “Oil Pollution Prevention” (see Attachment)

B.	Fuel Storage

1.	Purpose and application of the following system elements:

a.	Tanks

b.	Piping

c.	Pumps

d.	Accessory equipment

e.	Electronic monitors

2.	Operation, maintenance, and inspection of system elements

C.	Spill Prevention

1.	Potential spill sources

2.	Spill flow direction and impact on navigable waters

3.	Procedures to prevent spills, especially during fuel unloading

D.	Spill Control

1.	Secondary containment

2.	Safety valves

3.	Pump and equipment shutoff switches

4.	Use of catch basin inlet covers or other diversionary devices

E.	Spill Countermeasures

1.	Location and use of emergency phone numbers

2.	Location and use of fire extinguishers

3.	Location and use of spill cleanup kit

4.	Stopping the leak

ATTACHMENT

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS SECTION 112.1

THROUGH 112.20 - OIL POLLUTION PREVENTION

APPENDIX D

SPILL REPORTING FORM

(1 Page)

APPENDIX D

SPILL REPORTING FORM

| 1. GENERAL |
| --- |
| Name of Facility: National Weather Service St. Louis Weather Forecast Office | Address: 12 Missouri Research Park Drive St. Louis, Missouri 63304 |
| Completed By: | Organization: National Weather Service |
| Position: | Phone: |
| 2. SPILL INFORMATION |
| Date: | Time: |
| Location at Facility: | Quantity: |
| Substance Spilled: | Other: |
| 3. OUTSIDE NOTIFICATIONS |
| Agencies | Recorder at Outside Agency | Date and Time |
| Call 9-1-1 (or the local emergency agency), if there is an immediate emergency |  |  |
| NWS/NOAA: Mike Jacob: (301) 713-1838, Ext. 165 Olga Kebis: (301) 713-1838, Ext. 173 Kirt Grahl: (816) 426-3226, Ext. 470 Sherilyn Villegas: (816) 426-3925, Ext. 263 |  |  |
| EPA NATIONAL RESPONSE CENTER or U.S. COAST GUARD: (800) 424-8802 |  |  |
| Missouri Emergency Response Commission (573) 526-3315 |  |  |
| 4. INFORMATION ON SOURCE AND CAUSE |
| 5. DESCRIPTION OF ENVIRONMENTAL DAMAGE |
| 6. CLEANUP ACTION(S) TAKEN |
| 7. CORRECTIVE ACTION(S) TO PREVENT FUTURE SPILLS |

Note:	All information must be filled in.  If something is unknown, write “unknown.”

Copies must be submitted to the NWS/NOAA personnel listed above.

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS OF

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS,

SECTION 112.7, WITH THIS PLAN

(1 Page)

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS OF 40 CFR 112.7 WITH THIS PLAN

| CFR Citation | Item | Plan Location |
| --- | --- | --- |
| 112.7(a) | Spill History | Part I.B.4 |
| 112.7(b) | Potential Spill Prediction, Volumes, and Rates | Part I.B.5 and Table 2 |
| 112.7(c) | Containment and Diversionary Structures | Part I.B.2 and Part II.B.2 |
| 112.7(d) | Secondary Containment Impracticability | Not Applicable |
| 112.7(e)(1) | Drainage Control | Part I.B.3 |
| 112.7(e)(2) | Bulk Storage Tanks and Secondary Containment | See Subparts |
| 112.7(e)(2)(I) | Tank Compatibility with Its Contents | Part II.A.1 |
| 112.7(e)(2)(ii) | Diked Area Construction and Containment for Storage Tanks | Not Applicable |
| 112.7(e)(2)(iii) | Diked Area Inspection and Drainage of Rainwater | Not Applicable |
| 112.7(e)(2)(iv) | Corrosion Protection of Buried Metallic Storage Tanks | Not Applicable |
| 112.7(e)(2)(v) | Corrosion Protection of Partially Buried Metallic Tanks | Not Applicable |
| 112.7(e)(2)(vi) | Aboveground Tank Periodic Integrity Testing | Part IV.B.1 |
| 112.7(e)(2)(vii) | Control of Leakage through Internal Heating Coils | Not Applicable |
| 112.7(e)(2)(viii) | Tank Installation Fail-safe Engineered | Part II.A.1, B.1 |
| 112.7(e)(2)(ix) | Observation of Disposal Facilities for Effluent Discharge | Not Applicable |
| 112.7(e)(2)(x) | Visible Oil Leak Corrections from Tank Seams and Gaskets | Part II.A.3 & Appendix A |
| 112.7(e)(2)(xi) | Appropriate Position of Mobile or Portable Tanks | Not Applicable |
| 112.7(e)(3) | Facility Transfer Operations | See Subparts |
| 112.7(e)(3)(i) | Buried Piping Installation Protection and Examination | Part II.A.1 & Appendix A |
| 112.7(e)(3)(ii) | Not-in-service and Standby Terminal Connections | Not Applicable |
| 112.7(e)(3)(iii) | Pipe Support Designs | Not Applicable |
| 112.7(e)(3)(iv) | Aboveground Valve and Pipeline Examination | Not Applicable |
| 112.7(e)(3)(v) | Aboveground Piping Protection from Vehicular Traffic | Not Applicable |
| 112.7(e)(4) | Facility Truck Unloading Operations | Part II.A.2 |
| 112.7(e)(5-7) | Oil Production Facilities (Onshore) and Oil Drilling, Production, or Work over Facilities (On Shore and Offshore) | Not Applicable |
| 112.7(e)(8) | Inspections and Record Keeping | Part II.A.3 |
| 112.7(e)(9) | Security | See Subparts |
| 112.7(e)(9)(i) | Fencing | Part II.A.4 |
| 112.7(e)(9)(ii) | Flow Valves Locked | Not Applicable |
| 112.7(e)(9)(iii) | Starter Controls Locked | Not Applicable |
| 112.7(e)(9)(iv) | Pipeline Loading and Unloading Connections Securely Capped | Not Applicable |
| 112.7(e)(9)(v) | Lighting Adequate to Detect Spills | Part II.A.4 |
| 112.7(e)(10) | Training | See Subparts |
| 112.7(e)(10)(i) | Personnel Instructions | Part II.A.5 & Appendix C |
| 112.7(e)(10)(ii) | Designated Person Responsible for Spill Prevention | Page i |
| 112.7(e)(10)(iii) | Spill Prevention Briefings | Part IV.B.2 |

Note:	CFR	Code of Federal Regulations