Menomonie Energy Conservation Project Yr. 2002 Status Report

Date:  11/19/02

| Project # | Status | Description | Saving per Year $ | Cost for the Project | Payback period Months | Energy Reduction MM Btu/yr | Completion Date | Comments or status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | CANX | Climate control programming TCM (Grinder AHU) CANX | $25,000 | $75,000 | 36 | Currently being calculated | CANCELED MAY 2002 | Canceled – at this time it was decided that this project cost exceeds the payback period for the area. |
| 2 | CANX | Optical System – flash tank CANX | Na | Na | Na | Na | CANCELED MAY 2002 | Canceled – determined not to be a viable project. General maint. will be completed at this time |
| 3 | Comp. | Climate control for Master Tooling area – (slow down fan speeds when not in the area) | $14,093 | $17,489 | 14 | 1,202 | APR 2002 | Installed 3 VFD for the fans. Programmed fans to run at 50% on 2nd and 3rd shifts along with the weekend period. |
| 4 | Comp. | motion switches to the east / west hallway in Bld 3 to operate in 4 sections | $456 | $932 | 25 | 36.9 | FEB 2002 | Ron Shaw work with the electrical contractors to complete this installation. |
| 5 | Comp. | motion switches – 3C Packout area | $861 | $440 | 5 | 73.5 | JAN 2002 | Work Completed – no production issues in the area. |
| 6 | Comp. | motion switches – MRC HS area | $103 | $270 | 29 | 7.4 | JAN 2002 | Work Completed – no production issues in the area. |
| 7 | CANX | Upgrade the Evaporator to possibly a gas efficient unit (current is electric) | Na | Na | Na | Na | CANCELED MAR 2002 | Evaporator upgrade – This had no Energy Saving. The project was completed due to high maintenance savings. |
| 8 | CANX | Bld 2 hallway lighting motion switches (north / south) | $300 | $960 | 40 | 25.2 | CANCELED MAR 2002 | Payback is higher than anticipated also the traffic in the hallway has increased due to adding bld 10. |
| 9 | On-Hold | Programming pump speeds on all plating tanks to run motors slower. All currently have VFD (7 tanks) | $6,373 | $1,000 | 1 | 53.4 | On hold MAR 2002 | On hold – initial changes generated process problems. re-set the programs on the two test tanks. Need FE to continue. |
| 10 | On-Hold | Replace 2 Air Coolers with Chilled Water Cooling coil | $28,738 | $113,000 | 48 | 868 | On hold DEC 2001 | Continuing to estimate saving verse current productions schedules. |
| 11 | CANX | VFD on the AHU for S5 production area CANX | To be calculated | To be calculated | To be calculated | To be calculated | CANCELED AUG 2002 | No availability of VFD’s on site and the cost to purchase a new on along with the current schedule does not justify costs. |
| Project # | Status | Description | Saving per Year $ | Cost for the Project | Payback period Months | Energy Reduction MM Btu/yr | Completion Date | Comments or status |
| 12 | Site Utility | Investigate the possibility of raising the site CW temp from 42 deg to 46 deg | To be calculated | To be calculated | To be calculated | To be calculated | Update 11/19/02 from Chuck M | Project possibility Moved to the ECRP data base 11/19/02 |
| 13 | Site Utility | Programming, minor maint changes, and procedures updates for the Plant RO water system | $6,664 | na | 1 | 603 | 9/23/02 | Work completed |
| 14 | Not assing | Climate Control for AHU #23 in OSD | To be calculated | To be calculated | To be calculated | To be calculated | CANCELED 11/19/02 | Div Engineering is looking at modifying the space and adding different equipment. |
| 15 | Active | TPTC – Add a second LFL to the Ovens and reduce the need for so make-up air | To be calculated | To be calculated | To be calculated | To be calculated | Up date on 11/19/02 | Project possibility Moved to the ECRP data base 11/19/02 |
| 16 | Active | TPTC Lighting – upgrades with Motion Switches and fixtures | $519 | $229 | 4.8 | 44.24 | 10/30/02 | Work completed | Work completed |
| 17 | On hold | TPTC Lighting – upgrades with Motion Switches and fixtures | $122 | $300 | 28 | 6.2 | Update 11/19/02 from Ron Shaw | Project possibility Moved to the ECRP data base 11/19/02 |
| 18 | Active | TPTC climate control (adding 2 speed controls | To be calculated | To be calculated | To be calculated | To be calculated | No activity / no update 11/19/02 | Project possibility Moved to the ECRP data base 11/19/02 |
| 19 | Site Utilities | Lowering the site Steam pressure during the summer months | To be calculated | To be calculated | To be calculated | To be calculated | Update 11/19/02 from Chuck M | Project possibility Moved to the ECRP data base 11/19/02 |
| 20 | Site Utilities | Shut off the booster pump for the city water going to bld 3 | $2,296 | na | 1 | 196 | 9/23/02 | Work completed |
| Totals |  |  | $24,992 | $19,360 |  | 2163.04 |  |  |