July 22, 1994

Contract # TW0592

SPECIAL SPECIFICATION

SECTION 15711

FACTORY-FABRICATED COOLING TOWER

Page

PART 1 - GENERAL

1.01 Description.	2

1.02Related Work.	2

1.03Quality Assurance.	2

1.04References.	3

1.05Submittals.	3

1.06 Delivery, Storage, and Handling.	4

PART 2 - PRODUCTS

2.01Acceptable Manufacturers..	5

2.02 Induced-Draft, Crossflow Cooling Towers.	5

2.03 Motors.	6

PART 3 - EXECUTION

3.01 Inspection.	8

3.02 Installation/Application/Erection.	8

3.03 Field Quality Control..	9

3.04 Adjusting and Cleaning..	9

3.05 Commissioning..	9

3.06 Demonstration.	9

SPECIAL SPECIFICATION

SECTION 15711

FACTORY-FABRICATED COOLING TOWER

PART 1 - GENERAL

1.01	DESCRIPTION

A.  	This Section includes a factory-fabricated, induced-draft, crossflow cooling tower.

1.02	RELATED WORK

A.  	Section 01300

B.  	Section 15010

C.  	Section 15051

D.  	Section 15200

E.  	Section 15250

F.  	Section 15995

G.  	Condenser Water Treatment System by Sandia National Laboratory (SNL)

1.03	QUALITY ASSURANCE

A.  	Certify cooling tower's thermal performance according to Cooling Tower Institute (CTI) Standard 201.

B.  	Provide electric motors and electrical components required as part of factory-fabricated cooling towers that comply with applicable National Electrical Manufacturers Association (NEMA) Standards.

C.  	Install cooling towers according to National Fire Protection Association (NFPA) 70 "National Electrical Code."

1.04	REFERENCES

A.  	American Society of Heating, Refrigerating, and Air-Conditioning Engineers (ASHRAE) 1991 Heating, Ventilating, and Air-Conditioning (HVAC) Applications Handbook

B.  	American Society for Testing and Materials (ASTM) E84

C.  	ASTM A525

D.  	Code of Federal Regulations (CFR) Volume 10, Part 1910.23

E.  	CFR Volume 10, Part 1910.27

F.  	CTI Standard 201

G.  	NEMA Standards

H.  	NEMA MG-1, Motors and Generators

I.  	NFPA 70, National Electrical Code

1.05	SUBMITTALS

A.  	Make submittals according to this Section, Section 15010, and Section 01300.

B.  	Submit product data including rated capacities, pressure drop, fan performance data, weights (shipping, installed, and operating), installation instructions, startup instructions, and rating curves with selected points clearly indicated.

C.  	Submit shop drawings indicating dimensions, weight loadings, weight distribution, and clearances required around and between construction elements such as beams, columns, and walls.

D.  	Submit wiring diagrams for power supply wiring to cooling towers and ladder-type wiring diagrams for interlock and control wiring.  Clearly differentiate between factory-installed and field-installed wiring.

E.  	Submit maintenance data for each cooling tower.  Include parts lists for tower fill, water distribution system, fans, bearings, fan drives, controls, basin heaters, and all accessories.

F.  	Submit certified performance curves plotting leaving-water temperature (LWT) against wet-bulb temperature (WBT).

G.  	Submit calculations for the anchorage of the support beams to the slab.

A.  	See Section 15010.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

A.  	Provide cooling towers manufactured by one of the following:

1.  	Induced-Draft, Crossflow Cooling Towers:

a. 		Baltimore Aircoil Company.

b. 		The Marley Cooling Tower Company.

2.02	INDUCED-DRAFT, CROSSFLOW COOLING TOWERS

A.  	Description:  Induced-draft, crossflow cooling tower that is factory fabricated and factory assembled using manufacturer's standard design, materials, and construction according to published product information and these specifications.

B.  	Fan Description:  Propeller fan.

1.  	Fan Blade:  Cast aluminum with fixed pitch.

2. 	 Fan Drive:  Belt drive.

3.  	Fan Bearings:  Self-aligning ball bearings or bronze sleeve bearings.

4.  	Fan Motor:  Totally enclosed, air-over.

5.  	Motor Speed:  Single speed.

C.  	Hot-Water Distribution System:  For even distribution of water over fill material.

1. 	High density polyethylene basin, gravity-feed nozzles, and basin cover.

2.  	Single water inlet connection complete with a pre-strainer assembly and means to balance flow rates to the distribution basins.

D.  	Hot-Water Basin Control Valves:  For balancing flow to each distribution basin and for shutting off during servicing.

1.  	Valve Type:  Butterfly or globe valves.

E.  	Casing:  Hot-dipped galvanized steel with polymer coating or galvanized steel conforming to ASTM A 525 with Coating Designation G 210.

F.  	Collecting Basin:  Galvanized steel conforming to ASTM A 525, with Coating Designation G 210, or hot-dipped galvanized steel with polymer coating.

G.  	Fill Material:  Formed PVC, resistant to rot, decay, and biological attack with a maximum flame-spread rating of 5 per ASTM E 84 and fabricated, formed, and installed by the manufacturer to ensure that water breaks up into droplets.

H.  	Drift Eliminator Material:  Formed PVC resistant to rot, decay, and biological attack with a maximum flame-spread rating of 5 per ASTM E 84.

I.  	Louver Material:  Fiber-glass-reinforced plastic.

J.  	Water Level Control:  Manufacturer's standard mechanical make-up water valve, and a plastic or bronze float with an adjustable linkage.

K.  	Basin Heaters:  Of sufficient size to maintain basin water temperature at 40 degrees (deg.) Fahrenheit (F) (4 deg. Celsius [C]) when ambient temperature is 0 deg. F (minus 18 deg. C) and wind velocity is 10 mph.

L.  	Heater Type:  Electric immersion heaters.

1.  	Thermostat and Low-Water Cutout Switch:  Enclosed in weatherproof housing suitable for field wiring.

M.  	Handrails:  Galvanized-steel pipe rails that comply with requirements of 29 CFR 1910.23 (OSHA).

N.  	Ladders or Internal Walkways:  Galvanized-steel pipe rails that comply with requirements of 29 CFR 1910.27 (OSHA).

O.  	Safety Cage:  Galvanized-steel pipe rails that comply with requirements of 29 CFR 1910.27 (OSHA).

P.  	Lifting Devices:  Provide lifting devices at the base for rigging.

Q. 	See the Drawing Schedule for additional information.

2.03	MOTORS

A.  	General

1.  	Apply requirements below to motors covered by this Section except as otherwise indicated.

2. 	Motors 1 horsepower (hp) and Larger:  Polyphase.

3.  	Frequency Rating:  60 Hz.

4.  	Voltage Rating:  Determined by voltage of circuit to which motor is connected for the following motor voltage ratings (utilization voltages):

a.		Motors 1 hp and larger: 480 V circuit, 460 V - motor rating.

5.  	Service factors indicated for motors are minimum values and apply at frequency and utilization voltage at which motor is connected.  Provide motors which will not operate in service factor range when supply voltage is within 10 percent of motor voltage rating.

6.  	Capacity:  Minimum size as indicated.  If not indicated, sufficient to start and operate connected loads at designated speeds in indicated environment, and with indicated operating sequence, without exceeding nameplate ratings.  Provide motors rated for continuous duty at 100 percent of rated capacity.

7.  	Temperature Rise:  Based on 40 degrees centigrade ambient except as otherwise indicated.

8.  	Motor Speed:  Single.

B.  	Polyphase Motors

1.  	Squirrel-cage, induction-type, general-purpose conforming to the following requirements except as otherwise indicated.

2.  	NEMA Design Letter Designation:  "B," unless specifically designated "C" for high starting torque.

3.  	Energy Efficient Motors:  Nominal efficiency equal to or greater than that stated in NEMA MG 1, table 12-6C for that type and rating of motor.

4.  	Internal Thermal Overload Protection For Motors:  Protection automatically opens control circuit arranged for external connection.  Protection operates when winding temperature exceeds safe value calibrated to the temperature rating of the motor insulation.

5.  	Bearings:  Double-shielded, pre-lubricated ball bearings suitable for radial and thrust loading of the application, unless noted otherwise.

PART 3 - EXECUTION

3.01	INSPECTION

A. 	Inspect proposed route of moving cooling towers into place and verify that it is free of interferences.

B. 	Inspect elements and surfaces intended to support cooling tower.

C.  	Verify piping rough-in locations.

D.  	Verify suitability of branch circuit wiring.

E.  	Verify that each cooling tower conforms to regulatory and specification requirements.

F.  	Do not proceed until any unsatisfactory conditions have been corrected.

3.02	INSTALLATION/APPLICATION/ERECTION

A. 	 Install cooling towers according to equipment manufacturer's written instructions.

B.  	Install cooling towers plumb, level, and anchor.

C.  	Maintain manufacturer's recommended clearances for servicing and maintenance.

D. 	Piping Connections:  Maintain clearances for cooling tower service and maintenance.

E.  	Install flanged or union connections to cooling tower.

F. 	 Pitch piping down to drain into sump.

G.  	Install shutoff/balancing valves at cooling tower inlet connections when not provided as part of the cooling tower assembly.

H.  	Provide shutoff valves at cooling tower outlets.

I.  	Connect overflow drain and bleed lines to sanitary sewage system.

J.  	Electrical Wiring:  Install electrical devices furnished by manufacturer but not specified to be factory mounted, such as remote electronic water level controller, tower control panel, and remote basin water-heater control panel.  Furnish copy of manufacturer's wiring diagram submittal to Electrical Installer.

K. 	Cooling tower vendor shall provide W12 support beams and anchors to attach the cooling tower to the beams and the beams to a concrete slab.  The anchorage shall be designed for lateral and overturning seismic loads.  The lateral seismic load shall be equal to the weight of the cooling tower multiplied by 0.41.  Adhesive anchors shall be used to anchor the support beams to the slab.  Expansion anchors shall not be used.

3.03	FIELD QUALITY CONTROL

A.  	If CTI certification is unavailable then cooling towers shall be field tested according to CTI's standard field-testing method.

B.  	Manufacturer's Field Service:  Provide services of a factory-authorized service representative to supervise component field assembly and cooling tower installation, including piping and electrical connections.  Report results in writing.

3.04	ADJUSTING AND CLEANING

A.  	Balance condenser water flow to each tower inlet.

B.  	Adjust water level control for proper operating level.

C.  	Clean towers using materials and methods recommended by manufacturers.

D. 	Clean finishes to remove dust and dirt.

E.  	Touch up scratches in unfinished surfaces to restore corrosion resistance.

F.  	Touch up scratches in finished surfaces to restore finish.

3.05	COMMISSIONING

A.  	Provide labor, material, equipment, etc., required to facilitate the commissioning process.  Perform form tests and verification procedures required by the commissioning process when requested by the Commissioning Authority and directed by the General Contractor.  See Section 15995.

3.06	DEMONSTRATION

A.  	See Section 15995.

END OF SECTION