## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 738
EPA ID No. | IND000807107
Facility Name | Reilly Industries, Inc.
Facility Location
City | Indianapolis
State | IN
Unit ID Name/No. | Boiler 28K (**unit is now considered a sister unit to 737 (30K)**)
Other Sister Facilities | This unit is now considered a sister unit to 737 (30K)
Number of Sister Facilities | 0
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics | Watertube boiler. Babcock and Wilcox type FM; max thermal input of 36.8 MMBtu/hr; max operating pressure of 250 psig, steam production rate of 28000 lb/hr
Capacity (MMBtu/hr) | 36.8
Soot Blowing | Yes, 4 times/day, 5 minutes/event (run 3, cond 1)
APCS Detailed Acronym | None
APCS General Class
APCS Characteristics
Hazardous Wastes | Liq
Haz Waste Description | Pyridine and pyrindine-derived organic chemical production waste
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft) | 4.0016
Height (ft) | 43.0008
Gas Velocity (ft/sec) | 23.3864
Gas Temperature (°F)
Permitting Status | Tier I metals except Cr+6 (Tier III)
HWC Burn Status (Date if Terminated)

## cond
Cond Description
738C1
Report Name/Date | Revised Certification of Compliance Test Report for Boilers 70K, 30K, and 28K, August 21, 1996
Report Prepare | Spectrum Compliance Resources, Inc.
Testing Firm | Spectrum Compliance Resources, Inc., METCO Environmental, B3 Systems, Inc
Testing Dates | June 18-19 ,1996
Cond Dates | 1996-06-01
Cond Description | CoC, high feed rate
Content | PM, CO, Cr+6, HCl/Cl2
738C2
Report Name/Date | Revised Certification of Compliance Test Report for Boilers 70K, 30K, and 28K, August 21, 1996
Report Prepare | Spectrum Compliance Resources, Inc.
Testing Firm | Spectrum Compliance Resources, Inc., METCO Environmental, B3 Systems, Inc
Testing Dates | June 19-20, 1996
Cond Dates | 1996-06-01
Cond Description | CoC, min comb chamb temp
Content | CO

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2 |  |  | soot blow
1 | 738C1 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.0471 | 0.0456 | 0.1951 | 0.072
| CO (MHRA) | E1 | ppmv | y | 34.29 | 11.22 | 10.77 | 18.76
| CO (RA) | E1 | ppmv | y | 14.71 | 12.66 | 10.45 | 12.6067
| Chromium (Hex) |  | g/hr |  | 0.1216 | 0.0894 | 0.4536 | 0.1654
| HCl |  | g/hr |  | 0.907 | 0.454 | 0.907 | 0.719
| Cl2 |  | g/hr |  | 0.454 | 1.361 | 0.454 | 0.83
| Chromium (Hex) | E1 | µg/dscm | y | 7.9946 | 5.8813 | 29.8534 | 10.8794
| HCl | E1 | ppmv | y | 0.039821 | 0.019945 | 0.039863 | 0.031583
| Cl2 | E1 | ppmv | y | 0.019933 | 0.059791 | 0.019954 | 0.036458
| Total Chlorine | E1 | ppmv | y | 0.079687 | 0.13953 | 0.079771 | 0.1045
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  | 8039 | 8034 | 8188 | 8087
| O2 |  | % |  | 5.4 | 5.4 | 5.7 | 5.5
| Moisture |  | %
| Temperature |  | °F |  | 541 | 434 | 441 | 472
2 | 738C2 |  |  |  | R1 | R2 | R3 | Cond Avg
| CO (MHRA) | E1 | ppmv | y | 22.44 | 27.02 | 20.05 | 23.17
| Sampling Train | CO | E1
| Stack Gas Flowrate |  | dscfm
| O2 |  | % |  | 6.36 | 6.42 | 6.49 | 6.4233
| Moisture |  | %
| Temperature |  | °F

## feed
Feedstreams
| 738C1 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
* | Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2 |  | F3 |  | F3 |  | F3 |  | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | NG |  | NG |  | NG |  | NG |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW |  | MF |  | MF |  | MF |  | MF |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Waste Fuel |  | Waste Fuel |  | Waste Fuel |  | Waste Fuel |  | City Gas |  | City Gas |  | City Gas |  | City Gas |  | Spike |  | Spike |  | Spike |  | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/hr |  | 2158 |  | 2170 |  | 2164 |  | 2164 |  | 383 |  | 374 |  | 332 |  | 363
| Density | g/ml |  | 0.964 |  | 0.964 |  | 0.964 |  | 0.964
| Heat Content | Btu/lb |  | 14794 |  | 14773 |  | 14746 |  | 14771 |  | 21214 |  | 21214 |  | 21214 |  | 21214
| Thermal Feedrate | MMBtu/hr |  | 31.9255 |  | 32.0574 |  | 31.9103 |  | 31.9644 |  | 8.125 |  | 7.934 |  | 7.043 |  | 7.7007 | [9 empty] | 40.0504 |  | 39.9914 |  | 38.9534 |  | 39.6651
| MCB | lb/hr | [23 empty] | 3.29
| Ash | g/hr |  | 1027.8 |  | 1210.7 |  | 1266.3 |  | 1168.2667 | [8 empty] | nd | 1236.4 | nd | 1265.2 | nd | 1236.5 |  | 1246.0333
| Chlorine | g/hr |  | 313.24 |  | 314.98 |  | 294.48 |  | 307.5667 | nd | 0.18 | nd | 0.17 | nd | 0.15 |  | 0.17 |  | 320.62 |  | 426.97 |  | 370.63 |  | 372.74
| Chromium (Hex) | g/hr | [17 empty] | 0.2 |  | 0.2 |  | 0.2 |  | 0.228
| Antimony | g/hr | nd | 0.2447 | nd | 0.2461 | nd | 0.2356 |  | 0.2421 | nd | 0.0009 | nd | 0.0008 | nd | 0.0007 |  | 0.0008 | nd | 0.0043 | nd | 0.0043 | nd | 0.0045 |  | 0.0043667
| Arsenic | g/hr | nd | 0.0685 | nd | 0.0787 | nd | 0.0687 |  | 0.072 |  | 0.0006 |  | 0.0005 |  | 0.0005 |  | 0.00053333 | nd | 0.0068 | nd | 0.0072 | nd | 0.0075 |  | 0.0071667
| Barium | g/hr | nd | 0.0979 | nd | 0.0984 | nd | 0.0982 |  | 0.0982 | nd | 0.0325 | nd | 0.0317 | nd | 0.0281 |  | 0.030767 | nd | 0.0018 | nd | 0.002 | nd | 0.0018 |  | 0.0018667
| Beryllium | g/hr | nd | 0.0196 | nd | 0.0197 | nd | 0.0196 |  | 0.0196 | nd | 0.0001 | nd | 0.0001 | nd | 0.0001 |  | 0.0001 | nd | 0.0085 | nd | 0.0008 | nd | 0.0004 |  | 0.0032333
| Cadmium | g/hr | nd | 0.0489 | nd | 0.0492 | nd | 0.0491 |  | 0.0491 | nd | 0.0005 | nd | 0.0004 | nd | 0.0004 |  | 0.00043333 | nd | 0.0037 |  | 0.0014 | nd | 0.0022 |  | 0.0024333
| Chromium | g/hr |  | 0.31324 |  | 0.29529 |  | 0.373 |  | 0.327 | nd | 0.00075 | nd | 0.00073 | nd | 0.00065 |  | 0.00071 | nd | 0.23185 | nd | 0.23938 | nd | 0.22376 |  | 0.23167
| Lead | g/hr | nd | 0.0685 | nd | 0.0689 | nd | 0.0687 |  | 0.0687 | nd | 0.0002 | nd | 0.0002 | nd | 0.0001 |  | 0.00016667 | nd | 0.0082 | nd | 0.0082 | nd | 0.0078 |  | 0.0080667
| Mercury | g/hr |  | 0.0489 |  | 0.0295 |  | 0.0393 |  | 0.0392 | nd | 0.0002 | nd | 0.0002 | nd | 0.0002 |  | 0.0002 | nd | 0.0009 | nd | 0.0008 | nd | 0.0005 |  | 0.00073333
| Silver | g/hr | nd | 0.2643 | nd | 0.4626 | nd | 0.4712 |  | 0.3994 | nd | 0.0005 | nd | 0.0004 | nd | 0.0004 |  | 0.00043333 | nd | 0.0049 | nd | 0.0049 | nd | 0.0051 |  | 0.0049667
| Thallium | g/hr | nd | 0.2477 | nd | 0.2461 | nd | 0.2356 |  | 0.2421 | nd | 0.0001 | nd | 0.0001 | nd | 0.0001 |  | 0.0001 | nd | 0.0043 | nd | 0.0043 | nd | 0.0043 |  | 0.0043
| Stack Gas Flowrate | dscfm |  | 8039 |  | 8034 |  | 8188 |  | 8087 |  | 8039 |  | 8034 |  | 8188 |  | 8087 |  | 8039 |  | 8034 |  | 8188 |  | 8087
| O2 | % |  | 5.4 |  | 5.4 |  | 5.7 |  | 5.5 |  | 5.4 |  | 5.4 |  | 5.7 |  | 5.5 |  | 5.4 |  | 5.4 |  | 5.7 |  | 5.5
| Estimated Firing Rate | MMBtu/hr | [25 empty] | 39.8122 |  | 39.7874 |  | 39.7703 |  | 39.7932
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 67.5729 |  | 79.6472 |  | 83.3408 |  | 76.8536 | [8 empty] | 100 | 81.2873 | 100 | 83.2325 | 100 | 81.3795 | 100 | 81.9665 | 54.6065 | 148.8602 | 51.1006 | 162.8797 | 49.4047 | 164.7203 | 51.6096 | 158.8201
| Chlorine | ug/dscm |  | 20594.0109 |  | 20721.2954 |  | 19381.0316 |  | 20232.1126 | 100 | 11.8341 | 100 | 11.1836 | 100 | 9.8722 |  | 10.9633 |  | 21079.2101 |  | 28088.6771 |  | 24392.8 | 0 | 24520.2291 | 0.028389 | 41685.0551 | 0.022907 | 48821.1562 | 0.022548 | 43783.7037 | 0 | 44763.305
| Chromium (Hex) | ug/dscm | [17 empty] | 13.149 |  | 13.1572 |  | 13.1629 | 0 | 13.1564 | 0 | 13.149 | 0 | 13.1572 | 0 | 13.1629 | 0 | 13.1564
| Antimony | ug/dscm | 100 | 16.0878 | 100 | 16.19 | 100 | 15.5059 | 100 | 15.9279 | 100 | 0.059171 | 100 | 0.052629 | 100 | 0.04607 | 100 | 0.052623 | 100 | 0.2827 | 100 | 0.28288 | 100 | 0.29616 | 100 | 0.28725 | 100 | 16.4297 | 100 | 16.5255 | 100 | 15.8481 | 100 | 16.2678
| Arsenic | ug/dscm | 100 | 4.5035 | 100 | 5.1774 | 100 | 4.5215 | 100 | 4.7341 |  | 0.039447 |  | 0.032893 |  | 0.032907 | 0 | 0.035082 | 100 | 0.44707 | 100 | 0.47366 | 100 | 0.49361 | 100 | 0.47144 | 99.2095 | 4.9901 | 99.4213 | 5.6839 | 99.3481 | 5.048 | 99.3306 | 5.2406
| Barium | ug/dscm | 100 | 6.4365 | 100 | 6.4733 | 100 | 6.463 | 100 | 6.4576 | 100 | 2.1367 | 100 | 2.0854 | 100 | 1.8494 | 100 | 2.0238 | 100 | 0.11834 | 100 | 0.13157 | 100 | 0.11847 | 100 | 0.12279 | 100 | 8.6915 | 100 | 8.6903 | 100 | 8.4308 | 100 | 8.6042
| Beryllium | ug/dscm | 100 | 1.2886 | 100 | 1.296 | 100 | 1.29 | 100 | 1.2915 | 100 | 0.0065745 | 100 | 0.0065786 | 100 | 0.0065814 | 100 | 0.0065782 | 100 | 0.55883 | 100 | 0.052629 | 100 | 0.026326 | 100 | 0.2126 | 100 | 1.854 | 100 | 1.3552 | 100 | 1.3229 | 100 | 1.5107
| Cadmium | ug/dscm | 100 | 3.2149 | 100 | 3.2367 | 100 | 3.2315 | 100 | 3.2277 | 100 | 0.032873 | 100 | 0.026314 | 100 | 0.026326 | 100 | 0.028504 | 100 | 0.24326 |  | 0.0921 | 100 | 0.14479 | 80.8184 | 0.16005 | 100 | 3.4911 | 97.2549 | 3.3551 | 100 | 3.4026 | 99.1014 | 3.4163
| Chromium | ug/dscm |  | 20.594 |  | 19.426 |  | 24.5488 | 0 | 21.5229 | 100 | 0.049309 | 100 | 0.048024 | 100 | 0.042779 | 100 | 0.046704 | 100 | 15.243 | 100 | 15.7479 | 100 | 14.7266 | 100 | 15.2392 | 42.6132 | 35.8863 | 44.8468 | 35.2219 | 37.5638 | 39.3182 | 41.5278 | 36.8088
| Lead | ug/dscm | 100 | 4.5035 | 100 | 4.5327 | 100 | 4.5215 | 100 | 4.5192 | 100 | 0.013149 | 100 | 0.013157 | 100 | 0.0065814 | 100 | 0.010963 | 100 | 0.53911 | 100 | 0.53945 | 100 | 0.51335 | 100 | 0.53064 | 100 | 5.0558 | 100 | 5.0853 | 100 | 5.0414 | 100 | 5.0608
| Mercury | ug/dscm |  | 3.2149 |  | 1.9407 |  | 2.5865 | 0 | 2.5807 | 100 | 0.013149 | 100 | 0.013157 | 100 | 0.013163 | 100 | 0.013156 | 100 | 0.059171 | 100 | 0.052629 | 100 | 0.032907 | 100 | 0.048236 | 2.2 | 3.2873 | 3.2787 | 2.0065 | 1.75 | 2.6326 | 2.3236 | 2.6421
| Silver | ug/dscm | 100 | 17.3764 | 100 | 30.4326 | 100 | 31.0118 | 100 | 26.2736 | 100 | 0.032873 | 100 | 0.026314 | 100 | 0.026326 | 100 | 0.028504 | 100 | 0.32215 | 100 | 0.32235 | 100 | 0.33565 | 100 | 0.32672 | 100 | 17.7315 | 100 | 30.7813 | 100 | 31.3737 | 100 | 26.6288
| Thallium | ug/dscm | 100 | 16.2851 | 100 | 16.19 | 100 | 15.5059 | 100 | 15.9936 | 100 | 0.0065745 | 100 | 0.0065786 | 100 | 0.0065814 | 100 | 0.0065782 | 100 | 0.2827 | 100 | 0.28288 | 100 | 0.283 | 100 | 0.28286 | 100 | 16.5744 | 100 | 16.4794 | 100 | 15.7955 | 100 | 16.2831
| SVM | ug/dscm | 100 | 7.7185 | 100 | 7.7693 | 100 | 7.7529 | 100 | 7.7469 | 100 | 0.046022 | 100 | 0.039472 | 100 | 0.032907 | 100 | 0.039467 | 100 | 0.78237 | 85.4167 | 0.63155 | 100 | 0.65814 | 95.5551 | 0.69069 | 100 | 8.5469 | 98.9088 | 8.4404 | 100 | 8.444 | 99.6378 | 8.4771
| LVM | ug/dscm | 21.9515 | 26.3862 | 24.9943 | 25.8993 | 19.1416 | 30.3602 | 21.8728 | 27.5486 | 58.6207 | 0.09533 | 62.406 | 0.087495 | 60 | 0.082268 | 60.2981 | 0.088365 | 100 | 16.2489 | 100 | 16.2742 | 100 | 15.2466 | 100 | 15.9232 | 51.7125 | 42.7304 | 53.9555 | 42.261 | 46.1978 | 45.689 | 50.5098 | 43.5601
BIF Tier I Feedrate Limits
| Antimony | g/hr |  | 334
| Arsenic | g/hr |  | 2.56
| Barium | g/hr |  | 55577
| Beryllium | g/hr |  | 4.67
| Cadmium | g/hr |  | 6.23
| Chromium | g/hr |  | 3.68
| Lead | g/hr |  | 100
| Mercury | g/hr |  | 334
| Silver | g/hr |  | 3335
| Thallium | g/hr |  | 556
| Chlorine | g/hr |  | 4850

## process
Process Information
Cond Avg
738C1
Comb Temp | °F | 1620
Steam Production Rate | lb/hr | 30010
738C2
Comb Temp | °F | 1151.1
Steam Production Rate | lb/hr | 6700