## 25F nomo
Sedro Woolley (PSE)-Bothell (SCL)-Horse Ranch 230kV Line ***Includes Horse Ranch sect of Monroe-Snohomish 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 040
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3299.524
Gen Level |  | Trans | Worst | Limiting |  |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [6 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2634.41 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G3 | 100 | 775 | 2650.72 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2641.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G6 | 260 | 775 | 2479.69 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2650.72 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G9 | 525 | 775 | 2202.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2463.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G12 | 1000 | 775 | 995.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2475.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G15 | 1400 | 775 | 692.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2479.69 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G2 | 100 | 465 | 2641.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2187.89 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G5 | 260 | 460 | 2475.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2194.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G8 | 525 | 460 | 2194.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2202.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G11 | 1000 | 460 | 965.19 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 937.36 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G14 | 1400 | 460 | 683.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 965.19 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G1 | 100 | 140 | 2634.41 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 995.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G4 | 260 | 140 | 2463.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 676.54 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G7 | 525 | 140 | 2187.89 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 683.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G10 | 1000 | 140 | 937.36 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 692.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G13 | 1400 | 140 | 676.54 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450
G1
789

## 35F nomo
Sedro Woolley (PSE)-Bothell (SCL)-Horse Ranch 230kV Line ***Includes Horse Ranch sect of Monroe-Snohomish 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 040
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2622.872
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2511.76 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2527.34 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2516.1 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2353.85 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2527.34 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2075.41 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2338.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 723.22 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2346.37 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 564.13 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2353.85 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2516.1 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2063.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2346.37 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2067.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2067.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2075.41 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 714.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 707.78 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 556.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 714.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2511.76 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 723.22 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2338.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 550.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2063.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 556.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 707.78 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 564.13 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 550.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Sedro Woolley (PSE)-Bothell (SCL)-Horse Ranch 230kV Line ***Includes Horse Ranch sect of Monroe-Snohomish 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 040
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2380.476
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2415.24 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2433.98 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2421.58 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2264.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2433.98 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1841.54 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2249.31 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 628.51 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2257.48 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -222.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2264.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2421.58 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1776.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2257.48 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1813.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1813.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1841.54 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 620.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 614.79 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | -332.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 620.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2415.24 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 628.51 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2249.31 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | -444.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1776.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | -332.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 614.79 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | -222.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -444.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Sedro Woolley (PSE)-Bothell (SCL)-Horse Ranch 230kV Line ***Includes Horse Ranch sect of Monroe-Snohomish 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 040
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2902.996
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2423.87 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2441.08 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2434.31 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2270.67 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2441.08 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1888.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2258.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 638.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2264.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -587.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2270.67 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 2434.31 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1820.57 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2264.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1852.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1852.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1888.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 630.82 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 623.39 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | -690.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 630.82 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2423.87 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 638.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2258.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | -801.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1820.57 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | -690.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 623.39 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | -587.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -801.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Sedro Woolley (PSE)-Bothell (SCL)-Horse Ranch 230kV Line ***Includes Horse Ranch sect of Monroe-Snohomish 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 040
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3256.156
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2397.8 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2411.7 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2404.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2243.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2411.7 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1762.99 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2225.72 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 610.39 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2233.76 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -1131.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2243.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2404.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1700.81 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2233.76 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1730.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1730.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1762.99 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 605.67 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 597.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | -1246.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 605.67 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2397.8 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 610.39 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2225.72 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | -1350.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1700.81 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | -1246.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 597.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | -1131.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -1350.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Sedro Woolley (PSE)-Bothell (SCL)-Horse Ranch 230kV Line ***Includes Horse Ranch sect of Monroe-Snohomish 230kV Line (COV-CRES BYP @ COV)
G0 | 2634.41 | 2511.76 | 2415.24 | 2423.87 | 2397.8
G1 | 2641.46 | 2516.1 | 2421.58 | 2434.31 | 2404.56 | Season/Year: | WINTER 2009
G2 | 2650.72 | 2527.34 | 2433.98 | 2441.08 | 2411.7 | Direction: | North-to-South (NS)
G3 | 2463.64 | 2338.02 | 2249.31 | 2258.29 | 2225.72 | Case Loads: | Light Loads
G4 | 2475.06 | 2346.37 | 2257.48 | 2264.42 | 2233.76 | Outage: | 040
G5 | 2479.69 | 2353.85 | 2264.02 | 2270.67 | 2243.71 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2187.89 | 2063.28 | 1776.63 | 1820.57 | 1700.81 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2194.25 | 2067.92 | 1813.64 | 1852.56 | 1730.6 | Study Person: | FRP9899
G8 | 2202.71 | 2075.41 | 1841.54 | 1888.86 | 1762.99 | Source: | 040WINTER09v2NSL(SED-BOT-HR OUT)
G9 | 937.36 | 707.78 | 614.79 | 623.39 | 597.63
G10 | 965.19 | 714.96 | 620.02 | 630.82 | 605.67
G11 | 995.01 | 723.22 | 628.51 | 638.68 | 610.39
G12 | 676.54 | 550.01 | -444.14 | -801.43 | -1350.5
G13 | 683.26 | 556.35 | -332.03 | -690.59 | -1246.62
G14 | 692.26 | 564.13 | -222.21 | -587.9 | -1131.13
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Light Loads |  |  | 040 | Sedro Woolley (PSE)-Bothell (SCL)-Horse Ranch 230kV Line ***Includes Horse Ranch sect of Monroe-Snohomish 230kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3299.524 | 2634.41 | 2641.46 | 2650.72 | 2463.64 | 2475.06 | 2479.69 | 2187.89 | 2194.25 | 2202.71 | 937.36 | 965.19 | 995.01 | 676.54 | 683.26 | 692.26
35F | 2622.872 | 2511.76 | 2516.1 | 2527.34 | 2338.02 | 2346.37 | 2353.85 | 2063.28 | 2067.92 | 2075.41 | 707.78 | 714.96 | 723.22 | 550.01 | 556.35 | 564.13
45F | 2380.476 | 2415.24 | 2421.58 | 2433.98 | 2249.31 | 2257.48 | 2264.02 | 1776.63 | 1813.64 | 1841.54 | 614.79 | 620.02 | 628.51 | -444.14 | -332.03 | -222.21
60F | 2902.996 | 2423.87 | 2434.31 | 2441.08 | 2258.29 | 2264.42 | 2270.67 | 1820.57 | 1852.56 | 1888.86 | 623.39 | 630.82 | 638.68 | -801.43 | -690.59 | -587.9
70F | 3256.156 | 2397.8 | 2404.56 | 2411.7 | 2225.72 | 2233.76 | 2243.71 | 1700.81 | 1730.6 | 1762.99 | 597.63 | 605.67 | 610.39 | -1350.5 | -1246.62 | -1131.13

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2644.03 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -535.91 | -534.77 | 3339.25 | 2634.41 | 1325.24 | FULL
G1 | 2651.38 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -535.96 | -534.83 | 3275.35 | 2641.46 | 1354.96 | FULL
G2 | 2661.24 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -536.27 | -535.1 | 3292.63 | 2650.72 | 1381.54 | FULL
G3 | 2471.87 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -538.36 | -537.31 | 3337.43 | 2463.64 | 1307.36 | FULL
G4 | 2483.54 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -539.55 | -538.51 | 3272.9 | 2475.06 | 1340.29 | FULL
G5 | 2488.27 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -539.35 | -538.29 | 3291.18 | 2479.69 | 1363.62 | FULL
G6 | 2193.97 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -537.7 | -536.55 | 3339.31 | 2187.89 | 1274.83 | FULL
G7 | 2201.45 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -538.18 | -537.03 | 3275.86 | 2194.25 | 1302.93 | FULL
G8 | 2209.95 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -538.8 | -537.71 | 3293.24 | 2202.71 | 1333.16 | FULL
G9 | 937.65 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -531.22 | -528.69 | 3327.33 | 937.36 | 780.58 | FULL
G10 | 965.63 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -531.43 | -529.01 | 3263.27 | 965.19 | 823.54 | FULL
G11 | 995.54 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -531.15 | -528.83 | 3280.77 | 995.01 | 865.65 | FULL
G12 | 676.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -531.77 | -531.12 | 3339.14 | 676.54 | 810.44 | FULL
G13 | 682.53 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -530.62 | -529.94 | 3274.07 | 683.26 | 840.21 | FULL
G14 | 691.3 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -530.71 | -529.95 | 3291.13 | 692.26 | 875.43 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2521.5 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -525.07 | -524.01 | 2660.56 | 2511.76 | 1316.73 | FULL
G1 | 2525.55 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -522.32 | -521.24 | 2596.82 | 2516.1 | 1344.58 | FULL
G2 | 2536.83 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -524.18 | -523.12 | 2615.19 | 2527.34 | 1376.41 | FULL
G3 | 2345.79 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -522.66 | -521.63 | 2660.49 | 2338.02 | 1290.28 | FULL
G4 | 2354.28 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -523.55 | -522.53 | 2596.5 | 2346.37 | 1320.31 | FULL
G5 | 2362.24 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -523.65 | -523.04 | 2614.57 | 2353.85 | 1349.84 | FULL
G6 | 2069.13 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -525.27 | -523.82 | 2662.54 | 2063.28 | 1267.3 | FULL
G7 | 2073.26 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -524.09 | -522.63 | 2598.78 | 2067.92 | 1285.03 | FULL
G8 | 2080.95 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -523.96 | -522.52 | 2617.41 | 2075.41 | 1315.05 | FULL
G9 | 707.07 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -518.17 | -517.56 | 2649.7 | 707.78 | 709.6 | FULL
G10 | 714.36 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -518.12 | -517.48 | 2584.96 | 714.96 | 739.15 | FULL
G11 | 721.82 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -517.73 | -517.26 | 2602.56 | 723.22 | 769.63 | FULL
G12 | 549.07 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -516.91 | -516.26 | 2664.78 | 550.01 | 799.51 | FULL
G13 | 555.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -515.6 | -515.12 | 2600.26 | 556.35 | 828.7 | FULL
G14 | 562.92 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -515.13 | -515 | 2617.96 | 564.13 | 858.18 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2424.37 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -509.55 | -508.11 | 2420.98 | 2415.24 | 1299.57 | FULL
G1 | 2429.87 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -509.74 | -508.71 | 2357.25 | 2421.58 | 1318.89 | FULL
G2 | 2442.41 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -511.82 | -510.82 | 2375.09 | 2433.98 | 1356.63 | FULL
G3 | 2256.09 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -513.98 | -512.89 | 2420.68 | 2249.31 | 1277.75 | FULL
G4 | 2264.68 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -514.34 | -513.24 | 2357.01 | 2257.48 | 1307.49 | FULL
G5 | 2271.29 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -512.42 | -512.47 | 2374.76 | 2264.02 | 1332.68 | FULL
G6 | 1780.69 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -510.6 | -508.3 | 2419.91 | 1776.63 | 1134.61 | FULL
G7 | 1818.82 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -511.36 | -509.1 | 2356.39 | 1813.64 | 1181.44 | FULL
G8 | 1846.51 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -511.99 | -509.48 | 2375.26 | 1841.54 | 1214.8 | FULL
G9 | 613.09 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -506.52 | -504.74 | 2410.85 | 614.79 | 690.18 | FULL
G10 | 620.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -505.65 | -504.75 | 2346.29 | 620.02 | 718.36 | FULL
G11 | 628.04 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -506.11 | -504.7 | 2364.2 | 628.51 | 749.11 | FULL
G12 | -445.35 | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -2.71 | -155.96 | -155.95 | 2412.84 | -444.14 | 249.25 | FULL
G13 | -333.28 | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -2.71 | -156.01 | -155.93 | 2348.63 | -332.03 | 341 | FULL
G14 | -223.48 | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -2.71 | -156.04 | -155.96 | 2367 | -222.21 | 431.06 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2432.34 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -486.95 | -485.91 | 2944.52 | 2423.87 | 1255.1 | FULL
G1 | 2443.1 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -486.92 | -485.85 | 2879.82 | 2434.31 | 1293.09 | FULL
G2 | 2449.7 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -486.46 | -485.41 | 2897.68 | 2441.08 | 1321.7 | FULL
G3 | 2265.03 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -487.92 | -486.73 | 2943.73 | 2258.29 | 1240.96 | FULL
G4 | 2271.52 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -489.43 | -488.32 | 2879.63 | 2264.42 | 1268.14 | FULL
G5 | 2277.74 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -487.95 | -486.88 | 2897.7 | 2270.67 | 1293.63 | FULL
G6 | 1825.39 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -488.4 | -486.18 | 2943.54 | 1820.57 | 1113.06 | FULL
G7 | 1856.86 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -488.73 | -486.33 | 2879.66 | 1852.56 | 1157.49 | FULL
G8 | 1893.19 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -489.01 | -486.57 | 2897.76 | 1888.86 | 1203.79 | FULL
G9 | 622.37 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -482.97 | -482.33 | 2935.03 | 623.39 | 656.39 | FULL
G10 | 629.74 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -483.54 | -482.32 | 2869.35 | 630.82 | 686.63 | FULL
G11 | 638.69 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -483.6 | -482.33 | 2886.52 | 638.68 | 716.55 | FULL
G12 | -802.8 | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -2.71 | -140.02 | -139.98 | 2935.05 | -801.43 | 0.32 | FULL
G13 | -692.17 | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -2.71 | -140 | -139.95 | 2869.14 | -690.59 | 91.55 | FULL
G14 | -588.73 | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -2.71 | -140.11 | -140.04 | 2885.81 | -587.9 | 172.05 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2405.91 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -470.21 | -469.04 | 3297.63 | 2397.8 | 1244.06 | FULL
G1 | 2413.33 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -470.01 | -468.84 | 3232.95 | 2404.56 | 1272.94 | FULL
G2 | 2420.44 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -470.98 | -469.92 | 3250.78 | 2411.7 | 1296.64 | FULL
G3 | 2233.14 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -472.24 | -471.14 | 3296.96 | 2225.72 | 1212.4 | FULL
G4 | 2240.23 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -471.46 | -470.36 | 3233.22 | 2233.76 | 1242.65 | FULL
G5 | 2250.62 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -473.56 | -472.42 | 3250.23 | 2243.71 | 1274.49 | FULL
G6 | 1705.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -471.85 | -469.62 | 3295.52 | 1700.81 | 1041.21 | FULL
G7 | 1735.08 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -471.68 | -469.47 | 3230.77 | 1730.6 | 1083.53 | FULL
G8 | 1767.73 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -471.13 | -468.76 | 3248.92 | 1762.99 | 1127.76 | FULL
G9 | 596.74 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -467.81 | -465.85 | 3288.77 | 597.63 | 639.17 | FULL
G10 | 604.14 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -467.8 | -465.81 | 3223.15 | 605.67 | 669.02 | FULL
G11 | 609.94 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -86.17 | -467.65 | -466.24 | 3240.03 | 610.39 | 696.27 | FULL
G12 | -1349.14 | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -2.71 | -129.93 | -129.91 | 3291.08 | -1350.5 | -335.65 | FULL
G13 | -1245.57 | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -2.71 | -129.72 | -129.78 | 3223.76 | -1246.62 | -244.49 | FULL
G14 | -1130.54 | Branch ARLNGTON (42160) TO BEAVERLK (42162) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -2.71 | -129.8 | -129.82 | 3238.57 | -1131.13 | -150.16 | FULL
040WINTER09v2NSL(SED-BOT-HR OUT)