COMMUNICATIONS SITE PLAN

YELLOW BUTTE

ROSEBURG FIELD OFFICE

Prepared by the United States Bureau of Land Management

Roseburg Field Office

State of Oregon

Approved by: ____________________________________________    _______________

Field Manager						Date

YELLOW BUTTE COMMUNICATIONS SITE PLAN

I.	INTRODUCTION	3

A.	Terms and Definitions	3

B.	Purpose	4

C.	Site Description	4

D.	Area Served	4

E.	Access	5

F.	Site History and Development	5

G.	Goals and Objectives of Site Management Plan	5

II.	AUTHORITY AND DIRECTION	6

A.	Authority	6

B.	Relationship to Communications Site Lease	6

III.	GENERAL RESPONSIBILITIES	6

A.	The Bureau of Land Management	6

B.	Facility Owners and Facility Managers	7

C.	FCC and NTIA/IRAC	8

IV.	AUTHORIZED USES AND USERS WITHIN A FACILITY	8

A.	Exclusive Use of a Facility By a Single User	8

B.	Use by Multiple Users	8

V.	FEES	8

VI.	General Operation and Maintenance Direction	9

A.	Unique Resource Considerations at this Communication Site	9

B.	Wiring and Grounding	9

C.	Communications Equipment	10

D.	Cables and Transmission Line (Wave Guides)	12

E.	Radiation	12

F.	Utilities-Availability of and Requirements for:	13

G.	Sanitary Facilities	14

H.	Security and Law Enforcement	14

I.	Site Maintenance	14

J.	Inspections	15

K.	Fire Prevention and Hazard Reduction Requirements	15

L.	Access Maintenance and Restrictions	16

VII.	CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION	16

A.	New Facility Owner Responsibilities	17

B.	Construction Methods and Resource Protection	18

C.	Construction Inspection	19

D.	New or Remodeled/Expanded Buildings	19

E.	New or Remodeled/Expanded Towers	20

VIII.	SITE ASSOCIATION/ADVISORY GROUP	21

IX.	APPENDICIES	21

A.	Site Map	21

B.	Authorized Facilities	21

C.	Site Photographs	21

D.	Inspection Checklist	21

INTRODUCTION

## Terms and Definitions

The terms used in this communications site plan conform to the definitions listed in the October 27, 1995, Federal Register notice “Fee Schedule for Communications Uses on Public Lands” and clarifications provided in Bureau of Land Management Handbook 2860-1.  In the event of a conflict, between the plan and these sources, the Federal Register notice and the Bureau of Land Management Handbook will govern.

The words “lease” and “lessee” as used in this plan refer to the relationship between the Bureau of Land Management and the communications use leaseholder, the lessee.  The words “customer” and “tenant” refer to the relationship between the lessee and the occupants in the lessee’s facilities.

LEASE – A right-of-way (ROW) authorization issued to a communication Facility Owner or Facility Manager, allowing for the use of Public Lands to construct and or operate a communications facility and unless specifically prohibited, to sublease to occupants in that facility.

LEASEHOLDER OR LESSEE – Facility Owner/Facility Manager

CUSTOMER – Entities that pay a facility owner, facility manager or tenant for communications services and are not re-selling or broadcasting communications services to others

TENANT – A communications user who rents space in a communications facility and operates communication equipment for the purpose of re-selling, or broadcasting communications services to others for profit.

COMMUNICATIONS SITE – An area of BLM-managed public land designated through the land and resource management planning process as being used or as suitable for communications uses.  A communications site may be limited to a single communications facility, but most often encompasses more than one.  Each site is identified by name; usually a local prominent landmark, such as Yellow Butte Communications Site.

FACILITY MANAGER – The holder of a Bureau of Land Management communications use authorization who leases space for other communication users.  A facility manager does not directly provide communications services to third parties.

FACILITY OWNER – Individuals, commercial entities, organizations, or agencies that, owns a communications facility on Federal land; own and operate their own communications equipment; and hold a communications use authorization.

NON-BROADCAST – This category includes Commercial Mobile Radio Service (CMRS), Facility Managers, Cellular Telephone, Private Mobile Radio Service (PMRS), Microwave, Local Exchange Network, and Passive Reflector.

BROADCAST – This category includes Television Broadcast, AM and FM Radio Broadcast, Cable Television, Broadcast Translator, Low Power Television, and Low Power FM Radio.

## Purpose

This plan will be used by Bureau of Land Management officials, administering communications uses at Yellow Butte, existing lessees, and applicants desiring a lease or a lease amendment.  The plan will be kept updated by amending pages or sections of the plan rather than issuing a revised edition of the plan.  When a revision is necessary, a letter from the Roseburg Field Office enclosing a copy of revised pages or sections will amend the plan.  The amendments will be consecutively numbered.

Overall management direction for the administration of communications sites is outlined in the U.S. Code of Federal Regulations (CFR’s) and the BLM Handbook and applicable BLM Instructional Memoranda.  Specific direction for site management planning on designated communications sites is contained in BLM Handbook 2860-1.  Primary regulations and policy pertaining to issuance of ROW authorizations by the Bureau of Land Management are found in Title 43, Code of Federal Regulations (CFR), Sections 2801- 2803 and BLM Handbook 2860-1

The Roseburg Resource Management Plan (RMP) prepared in 1995 designates six existing communications sites including Yellow Butte as shown on Map 3-1 of the RMP/EIS covering 11 acres. These designations provide for two-way radio and microwave uses.  High power transmission uses are not considered compatible.  Existing sites should be fully utilized prior to development of new sites.  Yellow Butte is within a designated Late Successional Reserves. RMP direction provides for retaining and maintaining existing communication sites. Primary management of the current site is to assure historical government only, two-way radio and point-to-point microwave use.

No communications site plan has ever been prepared for this site.  This plan has technical standards for site specific management of the Yellow Butte Communications Site. This plan governs development and management of Yellow Butte and will be modified in the future as needs and conditions warrant.  Any future such uses must be designed, installed, operated, and maintained to be compatible and not interfere with the primary uses.  This site-specific plan is administrative in nature and is Categorically Excluded from further review under the National Environmental Policy Act (NEPA) (516.DM2, Appendix 1,1.7).  Any additional development of the site will be addressed in a appropriate a site-specific NEPA document.

## Site Description

The site is located on a peak identified as Yellow Butte which is located in the Roseburg Field Office area, in southern Oregon west of Yoncalla, Oregon in portions of Section 27, T. 23 S., R. 6 W, Willamette Meridian at approximately 43º 32’ North Latitude and 123º 24’ West. The elevation on top of the Yellow Butte Communications Site is approximately 2278 feet above mean sea level (msl).  A site map is provided as Appendix A.

## Area Served

This site does not currently serve a Ranally Metro Area, RMA and the largest community served is less than 25,000 population.  This information will be used for fee determination.

## Access

Access to Yellow Butte is from Interstate 5 to Yoncalla and then on Applegate Street to Hayhurst Road, State Route 24.  The route then continues south and west on Skelly Road to the Anderson Creek Road #71 to BLM roads 23-6-2.0, 23-6-15.1, and 23-6-12.0 to Yellow Butte.  This road provides access to all facility owners/managers and site users on Yellow Butte Communication Site.  All access is over public access except for a portion of private land in section 22.  Users must have a separate right-of-way from the private land owner.

## Site History and Development

The first communications facility ROW on Yellow Butte was issued for the Roseburg BLM radio repeater in 1986.  In 1989, a grant was issued to the Oregon State Police for a generator shelter and separate tower.  The OSP equipment is located in the BLM shelter.  A grant for a fire lookout to Oregon Department of Forestry was also issued in 1989 at this site.

## Goals and Objectives of Site Management Plan

1.	Manage the Yellow Butte Site as a government only, low power two-way radio and point-to-point microwave communications site.

2.	Manage communication equipment on the Yellow Butte Site to maintain the RF hazard within the public access, uncontrolled standards as defined by the FCC.

3.	Systematically develop the site to maximize the number of compatible uses while ensuring safety and protection of resources.  Development of new towers or buildings within each of the authorized owner’s facilities will be authorized only after their respective tower or building space area is filled to near capacity.

4.	Present a program for future growth, development and operation within the designated site.

5.	Help fulfill the public need for adequate communications sites.

6.	Protect the interests of leaseholders and site users by preserving a safe and electronically “clean” environment.

7.	Encourage the efficient development and use of space and facilities within the designated site, subject to the BLM’s goal to provide the best possible public service at reasonable cost.

8.	Achieve visual quality objectives by requiring design standards that are unobtrusive and utilizing earth tone colors and non-reflective surface material and stringent site maintenance requirements.

9.	Describe the BLM’s policy for authorizing road use and maintenance.

10. Developed new facilities only after the appropriate site-specific NEPA analysis and coordination with current leaseholders and users.  This future development must also be consistent with the Roseville RMP as approved.

11. New developments or future improvements must be designed to minimize impacts to the Lookout including viewshed and health/safety concerns of occupants of the Lookout tower.

11. Amend this Communications Site Plan as necessary to be consistent with the Roseburg RMP when it is revised.

AUTHORITY AND DIRECTION

## Authority

Bureau of Land Management authority to authorize communications uses on Public Land (administered by the BLM) is granted by the Federal Land Policy and Management Act of 1976, 90 Stat. 2776 (43 U.S. C. 1761-1771) and is reflected in Title 43, Code of Federal Regulations (CFR), Sections 2801- 2803 and WO IB 98-23.

Bureau of Land Management authority for communications site management planning is contained in Bureau of Land Management Handbook 2801-1, Plan of Development.  Direction on, and policy for communication use authorizations is contained in Bureau of Land Management Manual (BLM Manual) section 2860.

Authority for the issuance of authorizations and/or licenses for the transmission and reception of electronic radiation for communication purposes is granted by Congress and administered by the Federal Communications Commission (FCC) and/or the National Telecommunication and Information Administration – Interagency Radio Advisory Committee (NTIA/IRAC).

## Relationship to Communications Site Lease

This site plan will be incorporated into all leases now and/or in the future issued for this communications site and must be used in conjunction with the lease. PROVISIONS OF THE SITE PLAN ARE ENFORCED THROUGH THE LEASE. Each lessee is expected to include the requirements of the lease and the site plan into any documents, which describe the business relationship between the lessee and the lessee's tenants and customers. The lessee is responsible for enforcing those provisions

GENERAL RESPONSIBILITIES

## The Bureau of Land Management retains the responsibility for:

Issuing and amending leases and existing ROWs to Facility Owners and Facility Managers, only for the areas actually occupied by the authorized improvements.  Granting occupancy and use of Public Lands rests exclusively with the BLM, Title 43 CFR Sections 2801- 2803.  The issuance of a FCC license (authorization), or frequency assignment, does not authorize occupancy of Public Lands.

- Approving any new/modified facility(ies) at the site.

- Approving amendments to leases to qualified buyers of facilities on the site.

## Facility Owners and Facility Managers (or their designated representatives) are responsible for:

- Complying with their authorization and all sections of this Site Management Plan.

- Ensuring that all new facilities, expansions, or improvements are consistent with the Roseburg Field Office Planning Documents; any environmental document(s)/decisions for the site and this Communications Site Plan.

- Lessees are not authorize to place or have tenants place additional buildings, equipment shelters, and/or towers upon their lease area without written authorization from the Bureau of Land Management.  Owners of buildings, equipment shelters and/or towers must have their own authorization.  The primary configuration of a lease is one building and one tower.  Any additional buildings or towers must be authorized by the Bureau of Land Management and/or amended in the lease instrument.

- Ensuring facilities/equipment not complying with Federal/State/local laws/regulations/ ordinances will be removed or modified within one year of the approval of this plan.  Any modification needs pre-approval by the Bureau of Land Management.

- Keeping all facilities within the established limits of their authorized area.

- Providing the BLM, with the name, address and phone number for a local contact person.  The Facility Owner and Facility Manager and the contact person may be the same individual.  The contact person will be available for emergencies and will have the authority to make decisions about construction issues, facility maintenance and all equipment within the facility.

- Adhering to the Facility Owner/Manager Lease/ROW as follows:

  - Facility Owners and Facility Managers are authorized to rent building/tower space to tenants and/or customers without prior written approval from the Bureau of Land Management.

  - Tenants and/or customers using a facility covered by a Facility Lease/ROW will not have separate BLM Leases/ROWs to authorize the use.

  - Facility Owners and Facility Managers are responsible for complying with the terms and conditions of the Facility Lease/ROW.  Facility Owner/Managers are also responsible for ensuring that their tenants and customers are in compliance with the terms and conditions of the Lease/ROW, and applicable FCC or NTIA/IRAC license terms and conditions.

  - The Facility Owner and Facility Manager may not place any unreasonable restrictions nor any restriction restraining competition or trade practices on tenants and/or customers, or potential tenants and/or customers.

- Ensuring that all communications equipment is properly installed, operated, and maintained.

- Ensuring that all communication equipment meets ANSI, FCC and Bureau of Land Management regulations, guidelines and standards concerning radiation limitations by:

  - Monitoring radiation levels at their facility and;

  - Immediately correcting any radiation levels that are, or could be a hazard to human health. (FCC 47CFR sections 1.1307(b), 1.1310 and 2.1093) and FCC OET Bulletin 54, August 1999.

- Providing a certified copy of their use and the category of use along with the current phone numbers and addresses of all tenants and customers as of September 30th each year.  This report is due by October 15th.

- Keeping the premises around their buildings free of trash and debris.

- Placing the Lease/ROW holder’s name, address, phone number, and BLM Lease/ROW number on the door of their communications site building.

- Correcting interference problems.

## FCC and NTIA/IRAC are responsible for:

Frequency management.   The FCC and NTIA/IRAC are not normally responsible for the resolution of conflicts when the licensees or agencies are operating within the limits of the authorizations.

AUTHORIZED USES AND USERS WITHIN A FACILITY

## Exclusive Use of a Facility By a Single User

Single user facilities are discouraged.

## Use by Multiple Users

Use of facilities and improvements by more than one user will be required.  Facility owners will take the lead in this area and design their proposals to accommodate multiple uses of facilities and improvements.  This includes multiple uses of buildings, towers, back-up generators, grounding systems, fuel containers, access ways and parking areas.

Facility Owners and Facility Managers are not required to lease facility space to others if they can prove to the authorized Bureau of Land Management officer that:

- Space is not available;

- The use is incompatible with the existing facilities;

- Additional space is needed by the facility owner/manager;

- Additional users would violate system security needs; or,

- Potential interference is not resolvable.

FEES

The Bureau of Land Management will charge Facility Owners and Facility Managers annual fees based on the Fee Schedule for Communications Uses on Public Lands as adjusted annually.  These fees will be fair market value for the use of Public Lands.  Since this site is not within an RMA, Ranally Metro Area, the population Zone 9 will be used for these calculations unless something else is specifically agreed to in writing by the authorizing officer.

Fees that Facility Owners and Facility Managers may charge their tenants and “customers” are to be reasonable (consistent with, and not in excess of, other fees for similar facilities) and commensurate with the uses and occupancy of the facilities and services provided to tenants and “customers”.

Currently all fees for Federal, State, and local governments are exempt or waived as long as these agencies do not operate their facility for commercial purposes or profit.

General Operation and Maintenance Direction

## Unique Resource Considerations at this Communication Site

This site is adjacent to designated Late Successional Reserve as identified in the RMP.  The site is also within 35-50 mile zone (Zone 2) for the marbled murrelet (MAMU) and is within ¼ mile of unsurveyed, suitable MAMU habitat and is within MAMU critical habitat (CHU-OR-04-f).

In order to mitigate potential disturbance effects from any construction or upgrading activities to any facilities at this site to nesting MAMU, it is recommended that daily operating restrictions be applied from April 1st through August 5th.  The daily operating restrictions limit construction or upgrading activities to two hours after sunrise to two hours prior to sunset.

If other unique biological, cultural or historical resources are discovered, this plan will be amended to provide the appropriate resource protection consistent with the authorized uses.

## Wiring and Grounding

1.	All equipment is to be installed within existing buildings and on equipment racks that are grounded and shielded.  Grounding is to be installed in accordance with accepted standards.

2.	All electrical wiring and grounding must meet the “National Electrical Code” and applicable state codes.  All permanent wiring shall be installed in metallic conduit.  Surge protection shall be installed on all power distribution panels.

3.	Lightening protection “down” conductors installed upon communications towers shall be treated as “Transmission lines”.  Therefore, they shall have an insulating jacket.  Periodic bonding of the down conductor to the tower (Galvanized) steel shall be made with proper bonding connectors that are tin plated or made of brass.

4.	Each building is to have its own separate grounding system for all users in that structure.  Wherever practical, interconnection of individual grids and/or the simultaneous placement of a large sized copper ground wire with any new grounding systems that are buried on the site will be required.

5.	Site or facility grounding must be constructed of copper, with #2 AWG or larger wire or 2” or larger solid copper strap, connected to an adequate site/facility ground electrode system.  The site/facility ground electrode system shall be bonded to the power service entrance grounding electrode conductor.  Guy wires should also be grounded using manufacturers approved methods to preclude bi-metallic junction and corrosion.  All equipment on the site (buildings, towers, power units, transmitters, receivers, antennas, combiners, telephone systems, power cabinets, HVAC units, etc) must be connected to the site/facility ground by direct connection.  Electrical system ground wiring is required for electrical ground fault protection and circuit breaker coordination.  High power operations should use copper strap bonding in accordance with manufacturers specifications.  The grounding systems shall comply with applicable laws, codes and in accordance with standard engineering practice.  Below ground connections must use either an exothermic welding process (i.e. Cadweld, Thermoweld, etc.), copper wedge pressure devices (i.e. Ampact, Wrench-lock, etc.), or brazed copper connections in conjunction with a mechanical UL listed connector (to be used as a physical strength enhancement component).  Brazing by itself is not an acceptable method of bonding below earth grade (buried).

## Communications Equipment

Equipment Ownership

All equipment shall be labeled with:

- The owner’s name;

- Transmitter frequency(ies);

- A valid FCC, or IRAF, authorization;

- Transmitting power output(s); and

- A current 24-hour phone contact number.

Transmitting Equipment

All transmitters will have protective devices (shields, filters, isolation components), designed into or externally installed, to prevent interference to other users.  All transmitters will meet FCC licensing requirements.

Re-radiation of intercepted signals from any unprotected transmitter and its associated antenna system will be prevented by the use of appropriate filters (wide band and narrow band broadcast transmitters).

The direct radiation of out-of-band emissions (i.e. noise or spurious harmonics) will be reduced to a level such that they may not be identified as a source of interference as defined in the FCC Rules and Regulations (e.g. Part 90.209(e)).  If site noise (electromagnetic noise) becomes an issue, noise threshold limits will be established, and amended into the Site Plan.

All transmitters not in immediate use and not specifically designated as standby equipment shall be removed.  Loads connected to circulators are to be capable of dissipating the total power output of the transmitter.

Receiving Equipment

A bandpass device (cavity, crystal filter, etc.) is recommended at the input of all receiving devices.  Cavity filters, or other protective devices, may be used at receiver inputs to reduce interference.

Where duplexing is used, use of a notch type device should be avoided.  In situations where a notch type device is used, a bandpass filter must be used with the transmitter.

Tower

- Generally only one tower is authorized for each facility owner.  Facility Owners and Facility Managers may obtain permission to construct a second tower only after submitting evidence that demonstrates that their existing tower is completely filled and full use has been made of combining systems.

- All towers will be left unpainted, if they are dull, galvanized steel.  If paint is required, the Bureau of Land Management will approve only non-reflective colors from the Munsell Soil Color Chart, Standard Environmental Colors.  The exception is when the FCC requires red/white striping.

- No lights beacons or strobes will be allowed on towers (including antennas) less than 200 feet high.

- Maximum tower height (including antennas) for this site is 50 feet.

Antennas

            - The maximum antenna height (including tower) will be 50 feet.

            - Microwave (dish) antennas (other than ground mounted satellite dishes) will be a maximum of ten (10) feet in diameter.  The smallest diameter dishes are preferred if technically feasible.

            - All antennas must meet all OSHA safety standards.  If an antenna exceeds FCC public or occupations standards (see FCC OET Bulletin 57) it will be remedied within 24 hours after measures are taken or isolated (e.g., fencing, signing, relocation, lowering power levels are all possible remedies).  Ground measurements of RFR levels will be taken before mitigation measures are implemented.

            - Color(s) for dish antennas, or covers, must be pre-approved by the Bureau of Land Management.  White dish antennas and/or covers will not be approved.  Existing white dishes and covers must be repainted or replaced with dishes of approved color, as repairs or replacement become necessary.

            - Antennas will be treated for low to non-reflectance.

Interference

The responsibility for correcting interference problems is a matter for resolution between the Lease/ROW holder of the facility(ies), the user causing the interference, and the affected party(ies).  First users on a site have seniority with respect to the resolution of interference complaints.  Senior holders have an obligation to maintain their equipment to industry standards, to operate their systems in accordance with the terms of both the FCC license and NTIA/IRAC frequency authorization, and to comply with the Bureau of Land Management authorization.  New users on a site must correct, at their expense, interference problems that they create.  They must cease operation of the suspect equipment until the problem is corrected.  If interference problems cannot be resolved or corrected within a reasonable time, the new use that is causing the interference may be terminated and the equipment removed.

The Bureau of Land Management does not have authority for correcting interference problems, but can act as a mediator to help all affected parties.  Interference problems must be coordinated with the FCC or NTIA/IRAC whichever is appropriate.

Interference with law enforcement and/or emergency communications must be corrected immediately.  The operation of equipment covered by this Site Plan shall not interfere with United States Government radio or electronic operations already in existence on public land within two (2) miles of the site to which this authorization refers.  The user causing this interference, shall, at its own expense, take all action necessary to prevent or eliminate such interferences.  If it does not eliminate such interference within ten (10) days after receipt of notice from the Bureau of Land Management to do so, this use will be terminated.

If electromagnetic noise becomes an issue, noise thresholds will be established and this Site Plan will be amended accordingly.

## Cables and Transmission Line (Wave Guides)

All new cabling will be jacketed and shielded and shall either be flexible or semi-rigid type.  Existing substandard cables will be upgraded as repairs or replacement become necessary.

Cables will be properly installed and will be strapped and fastened down.  Use of ports at building entrance points will be kept to a minimum by use of combiners.

All transmission lines (wave guides) are to be supported in accordance with manufacturer’s specifications.

Double shielded braided, or solid shielded cable will be used.  No RG-8 type cable is permitted.  No connector-type adapters will be used on transmission lines.  Only correct connectors that will mate to connected devices are to be used.

Conduits will be shared when they service common areas and will be buried where possible.

## Radiation

All communications uses must meet ANSI, FCC and Bureau of Land Management regulations guidelines and standards concerning radiation limitations.

Monitoring radiation levels at the site is the responsibility of all site users and will occur at intervals to comply with FCC regulations and guidelines.  A copy of the monitoring report will be provided to the Bureau of Land Management within 30 days of its completion.

Onsite RFR measurements were made by RSI under contract with the BLM on March 26, 2004.  All readings on that day were well below the uncontrolled FCC/OSHA standards.  The actual study and report is available at the Roseburg Field Office for reference to actual findings, measurements, and warranties.  It is the responsibility of existing and future facility owners to monitor and maintain RFR levels below the uncontrolled standard.

Security fences with RFR notice signs are required around areas that exceed public use levels.    Raising higher power transmitting antenna on the tower or adding a taller tower may be necessary to eliminate RFR hazards.  Reducing power may also be required if other alternatives are not feasible. All fencing location and design or new tower construction must be pre-approved by the Bureau of Land Management.

Warning signs will comply with ANSI C95.2 color, symbol, and content conventions.  Contact information including name and telephone number will also be included on warning signs.

Lowering power levels for on-tower access during maintenance will be coordinated between affected users.

Any identified RFR radiation problems that are, or could be, a human health hazard must be corrected within 24 hours after measurement tests have been completed or be removed from the site by the site user(s).  If the proposed corrective action involves any new ground disturbance, it must be pre-approved by the BLM.

## Utilities-Availability of and Requirements for:

Commercial Electrical Power

No commercial power is provided to the site.

Telephone Service

No commercial telephone hardwire service this site.  All distribution and service connections would have to be buried.

Fuel Tanks

All facility owners are responsible for providing fuel storage and emergency power for their tenants.  No tenants will be authorized to have separate fuel tanks and/or generators. Each facility owner will preferably consolidate fuel storage into a tank large enough in size to accommodate all tenants.  At a minimum, tanks will be grouped together in a consolidated area adjacent to their facilities.  All fuel, storage tanks must meet current fire department, Federal, State and County safety and hazardous materials requirements.

- All tanks will be:

a.	Signed in red letters, “SMOKING OR OPEN FLAME PROHIBITED WITHIN 20 FEET”;

b.	In conformance with National Fire Protection Association (NFPA) requirements; and,

c.	Barriers which prevent vehicle collision with the tank must be installed and maintained.

## Sanitary Facilities

1.	Current sanitary facilities must be pre-approved by the Bureau of Land Management.  They will be maintained in a manner and location satisfactory to the Bureau of Land Management and within the requirements of the County Health Department.

## Security and Law Enforcement

The County Sheriff’s Department is the key law enforcement agency for the area.  They are responsible for most civil and criminal matters.  The Bureau of Land Management will be responsible for enforcing matters related to uses of BLM lands (e.g. resource protection issues).

Patrolling and policing for security purposes is the holder’s responsibility.  If holders desire to have the protection of extra fencing, Bureau of Land Management approval must be obtained first.  To reduce visual clutter and efficiently utilize existing space, fencing groups of buildings will be encouraged.

An access gate is currently on the access road.  If fencing is deemed necessary, the location of the fence and gates must be approved in advance by the BLM and must be adequate for Bureau of Land Management and County Fire Department access needs.

Fencing

1.	All fences must meet health and safety requirements.

2.	All fence locations and design require Bureau of Land Management pre-approval.  The standard fencing type will be chain-link (i.e. cyclone)

3.	The standard fence height will be eight (8) feet.

4.	Fencing will be designed and of a type to minimize interference issues.

5.	Fences will be signed with RFR notices if RFR is above public levels.

6.	All cyclone-type fencing materials will be galvanized.

## Site Maintenance

The objective of maintenance activities is to present a clean, neat, and orderly appearance at the site and have all of the authorized improvements safe for workers and the public.  All users will keep up the overall appearance of the site.

Miscellaneous debris remaining after any construction and/or equipment installation, removal or modification, is not only a hazard, but can cause interference or intermodulation problems.  In particular, all loose wire or metal objects are to be removed from the site.

The users of the Site will remove all graffiti within 10 working days of finding it.  If graffiti is on natural features (e.g. rocks), the graffiti will be removed in a method approved by the Bureau of Land Management Authorized Officer.

Holders will not be permitted to leave or dispose of trash, garbage or cut brush on BLM lands.  No outside trash or litter containers will be provided.  Site users (i.e. holders) will remove litter from the site as it is produced.

Policing of litter in common areas (i.e. areas between buildings and developed sites) is the shared responsibility of those holders bordering these areas.

During construction and/or maintenance, paintbrushes will not be cleaned off on the rocks around the site and excess materials (e.g. cement) will be removed from BLM land.

Peeling paint on buildings and/or towers will be re-painted within thirty (30) days of discovery by the Facility Owner or within 10 days of notification of the holder by the BLM.

## Inspections

Unless waived in writing by the Bureau of Land Management, the holder is to provide, annually, a certified inspection of the facilities and equipment covered by the authorization.  The inspection will include technical review that assures that authorized equipment is operating within the specifics of this Site Plan, the FCC authorization, ANSI Standards, and the manufacturer’s specifications.  In addition, the inspection must assure that the authorized equipment is secure, free of rust, properly grounded, and otherwise properly operated and maintained.  This inspection will also review general good "housekeeping". A copy of the inspection report, certified by a telecommunication specialist, is to be provided to the Bureau of Land Management within 30-days of completion.  Appendix D provides an example of the inspection checklist.

The Bureau of Land Management may also conduct un-announced periodic reviews to monitor for authorization compliance.

## Fire Prevention and Hazard Reduction Requirements

Facility owners and managers will be required to maintain to mineral soil, a minimum of (30) feet clearance around their buildings and a minimum of then (10) feet clearance around any propane tanks.  Identified threatened, endangered, or sensitive plant species must remain within the minimum clearance areas.

Smoking is prohibited in flammable vegetation areas.

Roof structures shall be kept reasonably clear of leaves, twigs, and other debris at all times.

No explosives will be stored at this site.  Flammable materials shall be stored in conformance with the requirements of local fire regulations.  Flammables will be placed in closed containers and stored away from sources of ignition and combustible materials.  If flammables are stored within a building, the building will be locked, properly signed and well ventilated.

Approved spark arresters will be required and maintained on all internal combustion engines.

At least one (1) U.L. rated 4 B:C dye chemical fire extinguisher is required inside each building.  Prior to each June, fire extinguisher(s) shall be inspected by holders and refilled, if necessary.

Any fire will be immediately reported to “911”, the nearest Bureau of Land Management office and./or County Sheriff.

Bureau of Land Management Officers will make periodic fire prevention inspections.  They will call to the holder’s attention any lack of compliance with the above regulations, plus any other existing hazards.  Compliance with these inspections is required within the time limits specified in the inspection report.

## Access Maintenance and Restrictions

Roads

Primary access is a graded road from the Skelly Road, County #71 to BLM roads 23-6-2.0, 23-6-15.1 and 23-6-12.0.   Annual road maintenance is performed as funds are available by the Bureau of Land Management.  If other road maintenance is necessary, it must be coordinated with the Bureau of Land Management and according to standards described by the authorizing officer.

Users who damage or disturb the access road, or any associated structures, such as ditches, culverts, roadside vegetation, signs and/or underground utilities or facilities, will be required to repair the road or associated structures, to conditions equal to or superior to those prior to any damage or disturbance.  This work may require appropriate NEPA analysis.

Interior Site Driveways/ Parking Areas

Roads within the communications site will be maintained by the site users.  Interior roads will be planned and approved during establishment of new facilities.  Interior roads will be maintained in a manner to allow only one entrance to the site.  Off-road vehicle use in and around the site is discouraged.

Road Closures

Roads on public land are subject to periodic closures to entry during periods of extreme fire danger, inclement weather, or wet conditions.  Authorized site users may use the site during these general closures if advance approval is obtained from the Bureau of Land Management.

CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION

## New Facility Owner Responsibilities

## In addition to the responsibilities listed in Section III, New Facility Owners and Facility Managers are responsible for:

1.	Submitting a complete application to the Roseburg Field Office prior to any new construction, or modifications to existing improvements  (ATTN: “Realty Specialist”).  The application must include:

- The appropriate cost recovery and application fees.

b.	A copy of the approved Site Plan Base Map showing all of the proposed (new) facilities including structures, towers, and auxiliary equipment;

c.	Completed drawings/plans prepared by a registered engineer and approved by the Bureau of Land Management;

d.	Identification of any microwave beam paths, a plot of their azimuth(s), and their proposed elevation(s) on the tower;

e.	Documentation that shows that proposed facilities will not be obstructing, or interfering with, any existing fixed point to point antennas, omni directional broadcast antennas, or microwave beam paths in the directions of primary population targets.  Proposed beam path needs must be shown on Site Plan Base Map; and,

f.	Any needed recommendations, changes or modifications to their original proposal, based on any required resource surveys and/or reports.

2.	Demonstrating that their proposals will not cause undue interference with any existing uses before the Bureau of Land Management can approve new facilities.  In addition, it is the applicant’s responsibility to show that any new facilities will make the most efficient use of the limited amount of space at the site.

3.	Showing their proposals will provide for future users without additional construction.

4.	Providing engineering and geotechnical investigations for development of specific foundation designs and grading plans.

5.	Providing an Erosion Control Plan prior to construction activities.  At a minimum, the Erosion Control Plan must include: sediment control, stipulations that cut/fill slopes will be graded and contoured to prevent erosion and/or excessive runoff, and recommendations for temporary erosion control measures, (e.g. netting, silt fences, swales, and/or sediment collection areas).

6.	Coordinating with other Federal (e.g., FCC and FAA), State and County agencies and obtain all required approvals and/or permits.

7.	Providing 30-day notice to all facility owners/managers at the site, as well as the Bureau of Land Management, of all new frequencies proposed for the site.  A completed BLM technical data sheet or equivalent must be sent with the 30-day notice to allow for comment of potential interference.  This would be for new frequencies for themselves and their tenants.

8.	Insuring that all written approvals have been obtained from the Bureau of Land Management prior to construction.  New and/or modified facilities will not obstruct existing fixed point-to-point antennas.

## Construction Methods and Resource Protection

Plans submitted by an applicant for any new construction or modifications shall specify provisions for soil rehabilitation measures including, but not limited to, soil replacement and stabilization and for proper handling of runoff from buildings, parking area, access roads, and undeveloped common areas.

The following methods and resource protection measures will be required to minimize impacts during construction:

1.	Avoid and protect sensitive resource areas as identified by the Bureau of Land Management.

2.	Compliance with the Erosion Control Plan.

3.	During construction and/or maintenance, paintbrushes will not be cleaned off on rocks around site and no marks of any kind (including survey) marks will be permitted on rocks.

4.	Minimize ground disturbance and vegetation removal as much as possible during construction activities.  All ground-disturbing activities require Bureau of Land Management pre-approval.

5.	Any extensive cut and fill slopes will be re-vegetated with native vegetation species pre-approved by BLM as soon as possible after construction.  If necessary, reseeding will be required until vegetation is successfully established as determined by the BLM.

6.	 No grading material will be cast off during construction/reconstruction activities. Excess soil can be used for fill material on road and/or building/tower pads.

7.	Temporary, on-site storage of construction materials will require pre-approval by the Bureau of Land Management.

8.	Construction materials and supplies, except for hazardous materials (see number 10. below) may be left unattended at the construction site at the end of each workday, but at the owner’s risk.

9.	Hazardous materials, including, but not limited to all fuels, oils, and lubricants are not to be left unattended at the site at any time.  During construction, these materials are to be removed from the site at the end of each workday, or temporarily stored inside a locked and signed building until the following workday.

10.	All surplus construction materials and/or waste debris must be removed from the site no later than thirty (30) days after construction has been completed.

11.	Any earth moving or heavy equipment (e.g. dozers, graders, cranes, backhoes, etc.) leaving the designated roadway and/or approved parking area(s) to perform authorized activities at the site, will be washed off prior to being brought onto public lands to prevent the introduction and spread of noxious weeds into the area.

12.	Pesticide Uses:   Use of any insecticide, herbicide, fungicide, rodenticide, or similar substances must be used according to all applicable State and Federal laws and regulations.  Prior to use of such substances on or near the authorized use, the lease holder shall obtain from the Authorized Officer approval of a written plan for such use.

## Construction Inspection

1.	All new construction, reconstruction, or major modification shall conform to the established technical standards and accepted engineering practices (i.e., the Uniform Building Code).

2.	Any construction inspections required by other applicable agencies are the responsibility of the holder.  Copies of completed inspections are to be provided to the Field Office Manager, either as they occur or as part of the final as-built plan.  Inspection information shall become a permanent part of the proponent’s Lease/ROW case file.

3.	The Holder agrees that corrective work detailed in Bureau of Land Management, or other agency required compliance inspections, would be completed by the scheduled completion date.  If the Holder disagrees or has questions about specific items, the Holder must contact the Bureau of Land Management in order that the disagreement or item may be resolved.

4.	A final set of as-built plans will be submitted to the Field Office Manager within 90 days of acceptance of structure (if contracted) or of completion date.

## New or Remodeled/Expanded Buildings

- Any new buildings must be designed to accommodate multiple users along with fitting into the physical environment as defined in a site-specific environmental analysis developed at the time of the proposal.

- Buildings are required to be one-story, flat roofed.  The roof must be metal or covered with metal to be fire resistant.  Roofs can be equipped with antenna support structures, such as poles and railings that can extend up to 25-feet above ground level.

- Facility Owners and Facility Managers are encouraged to construct the interior of their buildings in a modular fashion, so that they can:

a.	Sublease sections to others;

b.	Provide tenants and customers with internal separation and security;

c.	Reduce physical interference; and

d.	Increase management effectiveness.

- The following materials are approved for construction of new facilities (i.e. buildings)

#### a.	Floors – Concrete slab with drainage.

b.	Walls – Concrete block, metal or pre-fabricated concrete.

c.	Roof – Metal, or concrete, if painted to eliminate shiny surfaces, or other fireproof material as approved by the Bureau of Land Management.  Proposals for wooden roofs will not be approved.

d.	Partitions – If it is felt partitions are necessary in buildings, ensure they are constructed with fire resistant material (e.g., concrete block, reinforced concrete, or properly grounded expanded metal.

e.	Color – Proposed color for use on all exterior building surfaces must be pre-approved by the BLM. The goal of the color selection for the facilities is to make the building as inconspicuous as possible and make buildings located on the skyline look inconspicuous when viewed from a distance.  The intent is to reduce or eliminate glare from reflective and/or illuminated surfaces such as windowpanes, sheeting and reflective paints.  Non-reflective, BLM approved colors will be used on equipment buildings; refer to the Munsell Soil Color Chart, Standard Environmental Colors

- Building entry lights must:

a.	Only light the immediate area in the vicinity of the door;

b.	Be motion activated and have a limited time duration (e.g., 3-5 minutes); and

c.	Have a shielded beam that is pointed at the building door.

Requests for all-night (i.e. “dusk-to-dawn”) lighting, or entry lighting that would be visible from outside of the site will not be approved.

## New or Remodeled/Expanded Towers

- All new construction, reconstruction, and modifications to towers will be approved by the Bureau of Land Management prior to implementation.

- It is the applicant/holder’s responsibility to assure that a new, or modified, structure will not unduly interfere electronically or physically with any existing equipment at the site.  Towers must be spaced, so as to prevent ground level radiation and/or interference problems.  This must be clearly demonstrated in writing to the BLM prior to issuance of a Lease/ROW or amendment.

- All new towers will comply with current structural and safety specifications and design standards, including safety-climbing devices.  Towers should be as narrow and “open” as safety and structural integrity allow.  New towers will be designed using maximum wind, snow, and/or tower loading anticipated for the site.

SITE ASSOCIATION/ADVISORY GROUP

A Site Users’ Association may not be necessary due to the small number of authorized government users. If formed for the Yellow Butte Communications Site in the future, it would be responsible for participation in an access road maintenance agreement and maintenance of internal roads and parking areas.  The Site User’s Association will also be responsible for ensuring cooperation between users for on-tower access.  A Site Safety Officer would be identified within the Site User’s Association. The Site User’s Association would be expected to develop an RFR Plan/Agreement and recommend measures to reduce interference issues (e.g., through use of filters).

The goal of the Site User’s Association will also be to maximize the effective use of the site.  The objective of a sanctioned association will be to represent all site users as a group when dealing with the Roseburg BLM Field Office on matters relating to the Site administration.  The association will be able to work in cooperation with the Bureau of Land Management (BLM) to identify problems or opportunities and make recommendations to the BLM for any changes in management strategies at the site.  The association could also provide input to the BLM regarding the future addition of equipment and facilities at the site.  While the advice and recommendations of the association would not be binding on the BLM, the BLM could use the input for administration of the site.  The BLM would be a member of such a group and would help jointly develop the charter (i.e., the ground rules).

In absence of a formal Site User’ Association, the BLM may utilize a Site Advisory Group that can make suggestions and/or recommendations to specific problems associated with the administration of the site.

APPENDICIES

## Site Map

## Authorized Facilities

## Site Photographs

## Inspection Checklist

APPENDIX A

SITE MAP

(See associated AutoCAD Map on this website)

APPENDIX B

LESEE FACILITY TABLE

(See associated User’s Table on this Website)

|  | Auth # | Use | Building | Tower | Access/Parking | Other |
| --- | --- | --- | --- | --- | --- | --- |
| # 1 BLM | OR 17296 | PMRS | 8’x 10’ metal | 40’ lattice (35’ lattice to be removed) | Access and parking |  |
| # 2 Oregon State Police | ORE 44265 | PMRS | 8’x 10’ steel generator bldg | 40’ lattice | Access and parking |  |
| # 3 Oregon Dept of Forestry | ORE-44630 | Lookout |  | 55’ wood tower | Access and parking | Outhouse |

APPENDIX C

SITE PHOTOGRAPHS

(See associated Facility Photos on this Website)

APPENDIX D

INSPECTION CHECKLIST

“Yellow Butte Annual Technical Inspection”

Date Inspected: _____________________________   	Time Inspection: ________________________________

Permit Holder: ______________________________  	Authorization # _________________________________

Site Technician : ____________________________   	 Phone # _______________________________________

Number of Transmitters ______________________   	 License Posted _________________________________

Please mark the following Items as Acceptable (A) or Unacceptable (U).

Electrical Wiring ------------------- (A)     (U)        	Grounding --------------------- (A)     (U)

Equipment Installation ------------ (A)     (U)	Housekeeping ----------------- (A)     (U)

Building Repair -------------------- (A)     (U)	Tower Repair ------------------ (A)     (U)

Please mark the following Items as Yes (Y) or NO (N) or (NA)

Isolators ---------------------------- (Y)     (N)     (NA)	Circulators --------------------- (Y)     (N)     (NA)

Cavities ----------------------------- (Y)     (N)     (NA)	Terminators -------------------- (Y)     (N)     (NA)

Filters ------------------------------- (Y)     (N)     (NA)	Lightning Protection ---------- (Y)     (N)     (NA)

Comments: __________________________________________________________________________________

____________________________________________________________________________________________

Recommended Corrective Action:  ________________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

Required Corrective Action To Be Taken:  __________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

Committee Representatives:  _____________________________________________________________________

Bureau of Land Management Representatives: _______________________________________________________

Please make the required corrective action within the next 120 days.

Please make a written report of corrective action taken and submit to the BLM.  If  you should have any questions, please call the BLM office.