## 25F nomo
Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 012
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3339.4153
Gen Level |  | Trans | Worst | Limiting |  |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [6 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3416.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G3 | 100 | 775 | 3444.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3437.12 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G6 | 260 | 775 | 3292.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3444.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G9 | 525 | 775 | 3025 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3262.88 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G12 | 1000 | 775 | 2591.24 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3273.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G15 | 1400 | 775 | 2450.15 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3292.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G2 | 100 | 465 | 3437.12 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2980.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G5 | 260 | 460 | 3273.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3003.53 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G8 | 525 | 460 | 3003.53 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3025 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G11 | 1000 | 460 | 2582.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2564.85 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G14 | 1400 | 460 | 2434.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2582.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G1 | 100 | 140 | 3416.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2591.24 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G4 | 260 | 140 | 3262.88 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2422.98 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G7 | 525 | 140 | 2980.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2434.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G10 | 1000 | 140 | 2564.85 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2450.15 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G13 | 1400 | 140 | 2422.98 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450
G1
789

## 35F nomo
Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 012
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2661.816
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3306.93 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3313.93 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3311.81 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3144.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3313.93 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2872.89 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3139.95 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2459.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3133.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2314.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3144.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3311.81 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2852.82 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3133.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2861.37 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2861.37 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2872.89 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2443.15 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2442.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2300.32 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2443.15 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3306.93 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2459.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 3139.95 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2284.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2852.82 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2300.32 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2442.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2314.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2284.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 012
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2421.0347
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3193.38 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3211.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3192.61 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3053.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3211.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2771.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3037.33 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2349.52 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3039.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2198.1 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3053.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3192.61 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2752.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3039.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2758.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2758.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2771.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2343.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2334.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2192.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2343.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3193.38 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2349.52 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 3037.33 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2177.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2752.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2192.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2334.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2198.1 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2177.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 012
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2941.474
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3139.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3162.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3149.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3010.76 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3162.73 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2728.37 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2986.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2303.23 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3001.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2169.08 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3010.76 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 3149.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2708.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3001.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2716.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2716.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2728.37 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2295.4 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2285.09 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2153.36 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2295.4 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3139.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2303.23 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2986.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2140.12 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2708.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2153.36 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2285.09 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2169.08 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2140.12 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 012
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3293.1047
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3095.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3116.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3110.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2957.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3116.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2670.53 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2926.1 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2248.99 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2937.36 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2102.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2957.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3110.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2656.67 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2937.36 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2656.88 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2656.88 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2670.53 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2238.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2224.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2083.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2238.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3095.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2248.99 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2926.1 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2078.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2656.67 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2083.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2224.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2102.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2078.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
G0 | 3416.35 | 3306.93 | 3193.38 | 3139.46 | 3095.92
G1 | 3437.12 | 3311.81 | 3192.61 | 3149.01 | 3110.46 | Season/Year: | WINTER 2009
G2 | 3444.86 | 3313.93 | 3211.06 | 3162.73 | 3116.96 | Direction: | North-to-South (NS)
G3 | 3262.88 | 3139.95 | 3037.33 | 2986.01 | 2926.1 | Case Loads: | Light Loads
G4 | 3273.2 | 3133.21 | 3039.21 | 3001.86 | 2937.36 | Outage: | 012
G5 | 3292.47 | 3144.63 | 3053.97 | 3010.76 | 2957.75 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2980.97 | 2852.82 | 2752.6 | 2708.42 | 2656.67 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3003.53 | 2861.37 | 2758.42 | 2716.47 | 2656.88 | Study Person: | FRP9899
G8 | 3025 | 2872.89 | 2771.71 | 2728.37 | 2670.53 | Source: | 012WINTER09v1NSL
G9 | 2564.85 | 2442.06 | 2334.56 | 2285.09 | 2224.68
G10 | 2582.01 | 2443.15 | 2343.49 | 2295.4 | 2238.2
G11 | 2591.24 | 2459.06 | 2349.52 | 2303.23 | 2248.99
G12 | 2422.98 | 2284.77 | 2177.73 | 2140.12 | 2078.75
G13 | 2434.75 | 2300.32 | 2192.71 | 2153.36 | 2083.64
G14 | 2450.15 | 2314.46 | 2198.1 | 2169.08 | 2102.43
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Light Loads |  |  | 012 | Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3339.4153 | 3416.35 | 3437.12 | 3444.86 | 3262.88 | 3273.2 | 3292.47 | 2980.97 | 3003.53 | 3025 | 2564.85 | 2582.01 | 2591.24 | 2422.98 | 2434.75 | 2450.15
35F | 2661.816 | 3306.93 | 3311.81 | 3313.93 | 3139.95 | 3133.21 | 3144.63 | 2852.82 | 2861.37 | 2872.89 | 2442.06 | 2443.15 | 2459.06 | 2284.77 | 2300.32 | 2314.46
45F | 2421.0347 | 3193.38 | 3192.61 | 3211.06 | 3037.33 | 3039.21 | 3053.97 | 2752.6 | 2758.42 | 2771.71 | 2334.56 | 2343.49 | 2349.52 | 2177.73 | 2192.71 | 2198.1
60F | 2941.474 | 3139.46 | 3149.01 | 3162.73 | 2986.01 | 3001.86 | 3010.76 | 2708.42 | 2716.47 | 2728.37 | 2285.09 | 2295.4 | 2303.23 | 2140.12 | 2153.36 | 2169.08
70F | 3293.1047 | 3095.92 | 3110.46 | 3116.96 | 2926.1 | 2937.36 | 2957.75 | 2656.67 | 2656.88 | 2670.53 | 2224.68 | 2238.2 | 2248.99 | 2078.75 | 2083.64 | 2102.43

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3435.1 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -491.06 | -491.38 | 3368.77 | 3416.35 | 1695.25 | FULL
G1 | 3455.85 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -491.37 | -491.6 | 3305.11 | 3437.12 | 1733.47 | FULL
G2 | 3463.91 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -492.43 | -492.34 | 3324.37 | 3444.86 | 1765.57 | FULL
G3 | 3279.72 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -502.13 | -501.96 | 3366.86 | 3262.88 | 1672.62 | FULL
G4 | 3289.8 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -502.1 | -501.99 | 3303.33 | 3273.2 | 1708.07 | FULL
G5 | 3309.27 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -500.69 | -500.93 | 3322.2 | 3292.47 | 1745.34 | FULL
G6 | 2994.92 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -508.31 | -508.16 | 3368.74 | 2980.97 | 1619.44 | FULL
G7 | 3017.21 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -508.58 | -508.33 | 3304.66 | 3003.53 | 1669.8 | FULL
G8 | 3039.29 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -510.01 | -508.92 | 3322.97 | 3025 | 1709.85 | FULL
G9 | 2575.1 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -518.76 | -518.25 | 3377.95 | 2564.85 | 1590.12 | FULL
G10 | 2592.25 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -517.15 | -516.33 | 3314.76 | 2582.01 | 1637.52 | FULL
G11 | 2600.81 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -518.59 | -518.02 | 3333.43 | 2591.24 | 1670.67 | FULL
G12 | 2431.13 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -516.91 | -517.84 | 3394.39 | 2422.98 | 1668.82 | FULL
G13 | 2443.04 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -518.11 | -518.65 | 3332.08 | 2434.75 | 1703.57 | FULL
G14 | 2458.26 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -517.24 | -517.49 | 3351.61 | 2450.15 | 1742.13 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3324.52 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -486.97 | -486.15 | 2689.74 | 3306.93 | 1685.01 | FULL
G1 | 3329.27 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -485.28 | -485.73 | 2626.52 | 3311.81 | 1718.95 | FULL
G2 | 3331.2 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -484.55 | -484.75 | 2646.28 | 3313.93 | 1743.15 | FULL
G3 | 3155.48 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -499.59 | -499.94 | 2687.81 | 3139.95 | 1656.7 | FULL
G4 | 3148.63 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -495.35 | -495.03 | 2624.38 | 3133.21 | 1682.57 | FULL
G5 | 3160.51 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -494.4 | -494.14 | 2644.61 | 3144.63 | 1713.81 | FULL
G6 | 2865.94 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -499.38 | -502.65 | 2688.64 | 2852.82 | 1614.64 | FULL
G7 | 2873.48 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -500.67 | -500.47 | 2626.04 | 2861.37 | 1646.14 | FULL
G8 | 2885.48 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -500.2 | -499.99 | 2646.12 | 2872.89 | 1674.3 | FULL
G9 | 2450.21 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -506.21 | -505.42 | 2699.97 | 2442.06 | 1585.58 | FULL
G10 | 2451.37 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -503.03 | -502.28 | 2637.92 | 2443.15 | 1605.75 | FULL
G11 | 2467.55 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -504.58 | -503.84 | 2657.81 | 2459.06 | 1643.18 | FULL
G12 | 2292.45 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -505.57 | -505.39 | 2718.15 | 2284.77 | 1634.01 | FULL
G13 | 2307.59 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -505.79 | -505.35 | 2656.36 | 2300.32 | 1673.89 | FULL
G14 | 2322.89 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -505.54 | -505.07 | 2676.89 | 2314.46 | 1715.98 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3209.25 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -483.51 | -482.84 | 2447.44 | 3193.38 | 1655.84 | FULL
G1 | 3208.72 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -479.87 | -479.34 | 2385.19 | 3192.61 | 1681.39 | FULL
G2 | 3227.25 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -479.67 | -479.27 | 2404.08 | 3211.06 | 1724.56 | FULL
G3 | 3051.81 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -491.75 | -491.32 | 2445.97 | 3037.33 | 1631.49 | FULL
G4 | 3053.79 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -489.45 | -489.01 | 2383.89 | 3039.21 | 1660.29 | FULL
G5 | 3068.85 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -489.99 | -489.59 | 2403.22 | 3053.97 | 1692.69 | FULL
G6 | 2764.28 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -491.21 | -490.62 | 2447.84 | 2752.6 | 1589.3 | FULL
G7 | 2770.41 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -490.28 | -489.76 | 2385.33 | 2758.42 | 1618.73 | FULL
G8 | 2783.64 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -491.07 | -490.66 | 2405.83 | 2771.71 | 1647.24 | FULL
G9 | 2342.3 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -496.01 | -494.99 | 2460.14 | 2334.56 | 1552.26 | FULL
G10 | 2350.53 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -494.89 | -494.32 | 2397.11 | 2343.49 | 1592.84 | FULL
G11 | 2357.53 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -492.86 | -492.09 | 2417.86 | 2349.52 | 1615.65 | FULL
G12 | 2184.59 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -492.25 | -491.47 | 2478.69 | 2177.73 | 1618.62 | FULL
G13 | 2198.88 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -494.36 | -493.56 | 2416.38 | 2192.71 | 1646.8 | FULL
G14 | 2204.6 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -492.72 | -492.19 | 2436.55 | 2198.1 | 1683.34 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3154.99 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -461.06 | -459.54 | 2969.42 | 3139.46 | 1588.55 | FULL
G1 | 3164.61 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -459.98 | -463.43 | 2905.64 | 3149.01 | 1623.37 | FULL
G2 | 3178.32 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -460.92 | -460.62 | 2924.46 | 3162.73 | 1659.48 | FULL
G3 | 2999.87 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -470.28 | -470.01 | 2968.66 | 2986.01 | 1563.67 | FULL
G4 | 3015.73 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -470.72 | -469.57 | 2904.32 | 3001.86 | 1604.31 | FULL
G5 | 3024.8 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -469.81 | -469.42 | 2923.5 | 3010.76 | 1628.22 | FULL
G6 | 2719.75 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -470.99 | -470.04 | 2970.09 | 2708.42 | 1527.61 | FULL
G7 | 2727.98 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -470.24 | -469.79 | 2906.5 | 2716.47 | 1561.38 | FULL
G8 | 2739.58 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -470.15 | -469.83 | 2925.59 | 2728.37 | 1592.38 | FULL
G9 | 2292.58 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -473.24 | -472.65 | 2980.58 | 2285.09 | 1493.81 | FULL
G10 | 2302.06 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -472.69 | -472.11 | 2916.85 | 2295.4 | 1529.87 | FULL
G11 | 2310.98 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -470.78 | -470.51 | 2936.93 | 2303.23 | 1548.99 | FULL
G12 | 2146.4 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -472.23 | -471.42 | 2998.41 | 2140.12 | 1552.1 | FULL
G13 | 2159.82 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -473.63 | -472.83 | 2935.93 | 2153.36 | 1589.18 | FULL
G14 | 2174.95 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -472.79 | -472.06 | 2955.23 | 2169.08 | 1628.12 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3110.89 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -451.3 | -450.82 | 3322.75 | 3095.92 | 1541.31 | FULL
G1 | 3125.69 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -450.99 | -450.46 | 3257.85 | 3110.46 | 1592.02 | FULL
G2 | 3131.33 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -450.48 | -449.82 | 3276.22 | 3116.96 | 1624.2 | FULL
G3 | 2939.21 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -456.41 | -455.35 | 3320.82 | 2926.1 | 1526.43 | FULL
G4 | 2950.8 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -457.4 | -456.58 | 3256.32 | 2937.36 | 1557.77 | FULL
G5 | 2970.99 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -456.04 | -455.06 | 3274.2 | 2957.75 | 1600.87 | FULL
G6 | 2667.35 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -457.52 | -457.17 | 3322.07 | 2656.67 | 1495.68 | FULL
G7 | 2667.79 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -456.8 | -455.85 | 3258.45 | 2656.88 | 1513.04 | FULL
G8 | 2681.08 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -455.35 | -454.42 | 3276.5 | 2670.53 | 1557.13 | FULL
G9 | 2230.93 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -457.83 | -456.98 | 3333.77 | 2224.68 | 1439.95 | FULL
G10 | 2245.88 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -460.02 | -459.19 | 3268.62 | 2238.2 | 1489.06 | FULL
G11 | 2256.54 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -458.36 | -457.78 | 3287.25 | 2248.99 | 1524.79 | FULL
G12 | 2084.56 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -457.97 | -456.93 | 3350.18 | 2078.75 | 1514.74 | FULL
G13 | 2090.15 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -458.22 | -457.27 | 3286.59 | 2083.64 | 1545.29 | FULL
G14 | 2109.37 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -457.64 | -456.68 | 3304.98 | 2102.43 | 1598.49 | FULL
012WINTER09v1NSL