## General
General Notes
1) The following are the four primary options for the SMTF Cryo system presently considered
2) Additional options can be created by mix and match
3) The present cost numbers are for place holding and need revisions based on the scope and the equipment presently available
Actions Needed
1) Finalize the load requirements
2) Select the most possible system options for the study
3) Estimate the equipment available and their conditions
4) Revise the system and operating cost numbers
5) Make the final evaluation and select the recommended type of system for SMTF

## Requirements
Refrigeration Loads Requirement |  |  | Present | P_Carnot req. |  | Notes
|  |  | load | KW
4.5K Refrigeration | W |  | 300 | 22.7
4.5K Liquefaction | g/s |  | 2 | 13.7 | ? | Corrector leads may require some flow.
But probably not this much.
2 K Refrigeration (15.5 g/s) | g/s |  | 300 | 42 | ?? | 4.5K, 3 atm sup.,10K atm ret.
2 K Liquefaction (SCB-unbalence flow) | g/s |  | 1.6 | 10.6 | ? | SCB Hp_Unbalence flow (10% of Lp flow)
Sheld Refrigeration | W |  | 5000 | 37.5 | Pr. Drop? | We will assume a small pressure drop now.
But we should estimate pressure drops for the system.
Load P_Carnot req. |  |  |  | 126.5 | Max ?
Cold Copressors adder |  |  |  | 8.7 |  | If Option -2 is used (Two stage17 g/s)
Distribution losses | 0% | ? |  | 0 |  | We have included distribution and
Control | 0% | ? |  | 0
Total P_Carnot req. | KW | ? |  | 135.2
System Carnot Eff | 15% | ?
Compressor Input | KW |  |  | 901.3333
Motor Input | KW |  |  | 1001.4815
Motor Size | BHP |  |  | 1624.024

## Carnot_Analysis
Carnot Analysis of the Loads
P | (atm) | 1
T0 | (K) | 300
h | (J/g) | 1573.5188
s | (J/g-K) | 31.5843
Load |  | p [atm] | T [K] | h [J/g] | s [J/g-K] | Dh [J/g] | m | P_Carnot
| W | [5 empty] | g/s | KW
4K | 300 | 3 | 4.5 | 11.7913 | 3.6167
|  | 1 | 4.3 | 31.4306 | 8.6352 | 19.6393 | 15.2755 | 22.698
2K | 300 | 3 | 2.5 | 5.7377 | 1.9121
|  | 0.03 | 2 | 25.0592 | 12.6488 | 19.3215 | 15.5267 | 49.7119
|  | 3 | 4.5 | 11.7913 | 3.6167
|  | 1 | 10 | 65.495 | 13.808 | 53.7037 | 13.9741 | 41.9737 | Kinney System
|  | 1 | 300 | 1573.5188 | 31.5843 | 1508.0238 | 1.5527 | 10.6025 | 52.5763
|  | 3 | 4.5 | 11.7913 | 3.6167
|  | 1 | 15 | 92.2375 | 15.9784 | 80.4462 | 13.9741 | 50.6989 | CC System
|  | 1 | 300 | 1573.5188 | 31.5843 | 1481.2813 | 1.5527 | 10.6025 | 61.3014
40 | 5000 | 3 | 20 | 117.5238 | 15.1612 |  | 16 |  | 20K
|  | 15 | 80 | 434.5029 | 19.086 |  | 8 |  | 80K
|  | 3 | 40 | 223.0475 | 18.8234 |  | 24 |  | Mix to shield load
|  | 1 | 80 | 430.9705 | 24.7197 | 207.923 | 24.0474 | 37.5368 | From shield load
300-4K |  | 1 | 4.2 | 9.9035 | 3.5475
|  | 1 | 300 | 1573.5188 | 31.5843 | 1563.6154 | 2 | 13.6949 | Liquefaction Load

## SSCL_4KW_Plant
SSCL_4KW_Plant System Capacity |  | Test Capacty & Efficiencies
Refrigeration Loads | Carnot Power req. | System | P_Carnot@100% | Carnot Efficiency | Input Power
(2 first and second stage compressors) | W / unit load | Capacity | KW | % | KW
4.5K Refrigeration (W) | 70 | 3500 | 245 | 19 | 1406
4.5K Liquefaction (g/s) | 6800 | 35 | 238 | 15
50R (W) / 50L (g/s) |  | 2KW + 20 g/s | 300 | 20
Refrigeration Loads | Carnot Power req. | System | P_Carnot@50% | Carnot Efficiency
(1 first and second stage compressors) | W / unit load | Capacity | KW | %
4.5K Refrigeration (W) | 70 | 1450 | 101.5 | 13.8 | 703
4.5K Liquefaction (g/s) | 6800 | 18 | 122.4 | 15.6
50R (W) / 50L (g/s) |  | 0.8KW + 8 g/s | 103 | 14.8
Estimated Input Power @ |  |  | 130 |  | 1200

## System_Cost
SMTF_Cryo_System
|  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
System Cost ($)
Helium Gas Storage (HGS) |  | 210000 | 210000 | 210000 | 210000
Main Compressor System (MCS) |  | 360000 | 360000 | 1000000 | 1000000
Main Cold box System (MCB) |  | 415000 | 415000 | 1200000 | 1200000
Process Vacuum System (PVS) |  | 200000 | 200000 | 300000 | 300000
Sub Atm Coldbox (SCB) |  | 200000 | 200000 | 500000 | 500000
Distribution Box (DBX) |  | 0 | 185000 | 0 | 185000
Purifier Compressor (HPC) |  | 200000 | 200000 | 200000 | 200000
Purifier Coldbox (HPB) |  | 200000 | 200000 | 200000 | 200000
Lhe_Dewar (LHD) |  | 150000 | 150000 | 150000 | 150000
Ln2 System (Ln2) |  | 300000 | 300000 | 300000 | 300000
Vacuum System (VAC) |  | 68000 | 68000 | 68000 | 68000
Utilities (UTL) |  | 235000 | 235000 | 235000 | 235000
Civil |  | 1155000 | 1155000 | 1055000 | 1055000
Controls |  | 300000 | 300000 | 300000 | 300000
Items Total |  | 3993000 | 4178000 | 5718000 | 5903000
System Engineering |  | 500000 | 500000 | 300000 | 300000
System Fabrication Labor |  | 500000 | 500000 | 300000 | 300000
Installation & Comissioning |  | 500000 | 500000 | 300000 | 300000
Field Total |  | 1500000 | 1500000 | 900000 | 900000
Total ($) |  | 5493000 | 5678000 | 6618000 | 6803000
Contengency (%) | 10 | 549300 | 567800 | 661800 | 680300
Final Total |  | 6042300 | 6245800 | 7279800 | 7483300

## Opper_Cost
SMTF_Cryo_System_Opperating_Cost
|  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
MCS Electric Power | KW | 1200 | 1200 | 1000 | 1000
PVS Electric Power (Two Kinnes) | KW | 200 | 200
PVS Electric Power (Screw Comp) | KW |  |  | 100 | 100
Purifier Comp Electric power | KW | 100 | 100 | 100 | 100
Auxilaries | KW | 200 | 200 | 200 | 200
Elec. Total | KW | 1700 | 1700 | 1400 | 1400
Ln2 | gal/hr | 100 | 100 | 100 | 100
Elec Power Cost | $/Kw | 0.05
Ln2 Cost | $/Gal | 0.25
Elec. Operating Cost /Hr | $ | 85 | 85 | 70 | 70
Ln2 Operating Cost /Hr | $ | 25 | 25 | 25 | 25
Operating Cost /Hr | $ | 110 | 110 | 95 | 95
Operating Cost /Day | $ | 2640 | 2640 | 2280 | 2280
Operating Cost /Month | $ | 79200 | 79200 | 68400 | 68400
Operating Cost /Year | $ | 963600 | 963600 | 832200 | 832200

## HGS
Helium Gas Storage (HGS)
|  |  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
| Number | Unit Cost
He Gas Storage tanks (30,000 gal) | 3 | 50000 | 150000 | 150000 | 150000 | 150000
Instrumentation & Controls | 3 | 5000 | 15000 | 15000 | 15000 | 15000
Piping & Valves | 3 | 15000 | 45000 | 45000 | 45000 | 45000
Total |  |  | 210000 | 210000 | 210000 | 210000

## MCS
Main Compressor System (MCS) SSCL_4KW for Option-1 and New System for Option-2
|  |  |  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
Equipment
| Number | Unit Cost | Total Cost ($)
Compressor Skid First Stage parts | 2 | 20000 | 40000
Compressor Skid Second Stage parts | 2 | 25000 | 50000
Motor Control Cent first stage | 2 | 25000 | 50000
Motor Control Cent second stage | 2 | 40000 | 80000
Motor Control Cent Transition Section | 1 | 12000 | 12000
System Piping & Fittings | 1 | 50000 | 50000
Oil Removal & Gas Man Skid | 1 | 63000 | 63000
Gas Management Valves | 4 | 7000
Coalescer & Vessels | 4 | 0
Charcoal & Vessel | 1 | 0
Instrumentation P,T, and Flow | 1 | 20000
Oil Rem & Gas Man Piping | 1 | 15000
Installation Comp, Oil rem (Crane etc) | 1 | 15000 | 15000
Equip. Total |  |  | 360000 | 360000 | 360000 | 1000000 | 1000000

## MCB
Cold Box System (MCB) SSCL_4KW for Option-1 and New System for Option-2
Cold Box Equipment |  |  |  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
| Quantity | Unit Cost ($) | Total Cost ($)
Coldbox
Expander rotors | 4 | 0 | 0
80K & 20K Regen system | 1 | 60000 | 60000
Warm Valves & Actuators | 1 | 50000 | 50000
Cold Valves & Actuators | 1 | 50000 | 50000
Instruments P, T, Flow, Level | 1 | 100000 | 100000
Purity monitoring Equipment | 1 | 20000 | 20000
System Piping | 1 | 50000 | 50000
Other Parts (Elec Boxes, wiring etc) | 1 | 50000 | 50000
Structure around CBX | 1 | 20000 | 20000
Installation Cbx,pods(Crane etc) | 1 | 15000 | 15000
Spares
Equip. Total |  |  | 415000 | 415000 | 415000 | 1200000 | 1200000

## PVS
Process Vacuum System (PVS) Kinneys for Option-1 and new sub atm. compressor for Option-2
| Option-1A | Option-1B | Option-2A | Option-2B | Notes
Kinney System | 200000
Sub Atm Screw Comp Skid |  |  | 300000
Total
| 200000 | 200000 | 300000 | 300000

## SCB
Sub Atm. Cold Box (SCB) Option-1 Uses Kinneys and Option-2 uses CC's
|  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
Heat exchangers | 100000
Coldbox | 25000
Instrumentation & Controls | 25000
Piping & Valves | 50000
Total | 200000 | 200000 | 200000 | 500000 | 500000

## Dist_Box
Distribution Box (DBX)
|  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
Heat exchangers | 30000
Phase seperators with coils | 30000
Coldbox | 25000
Instrumentation & Controls | 50000
Piping & Valves | 50000
Total | 185000 | 0 | 185000 | 0 | 185000

## Purifier_Comp
Purifier Compressor (HPC)
|  |  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
Recovery Compressor | 1 | 125000
Gasmanagement |  | 30000
Instrumentation |  | 20000
Piping |  | 25000
Total |  | 200000 | 200000 | 200000 | 200000 | 200000

## Purifier_CBX
Purifier Cold Box (HPB)
|  |  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
Purifier Cold Box (2beds) | 1 | 150000
Regen |  | 25000
Piping & Valves |  | 25000
Total |  | 200000 | 200000 | 200000 | 200000 | 200000

## Lhe_Dewar
Liquid Helium Dewar (LHD)
Lhe |  |  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
LHe_Dewar | 1 | 70000
Dewar Neck Can & Valves |  | 40000
Heater, Conrols & Instrumentaion |  | 20000
U-Tubes |  | 20000
Total |  | 150000 | 150000 | 150000 | 150000 | 150000

## Ln2
Liquid Nitrogen (LN2)
|  |  |  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
LN2
Ln2_Dewar | 1 | 250000
Gn2_Vap | 1 | 15000
Controls |  | 10000
Piping |  | 25000
300000
Total |  |  | 300000 | 300000 | 300000 | 300000 | 300000

## Vacuum
Vacuum (VAC)
|  |  |  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
Vac System
Shell Vac | 1 | 6000
Guard Vac | 1 | 6000
Spare | 1 | 6000
Instrumentation |  | 25000
Piping & Valves |  | 25000
Total |  |  | 68000
Total |  |  | 68000 | 68000 | 68000 | 68000 | 68000

## Utilities
Utilities (UTL)
|  |  |  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
Power
Substation | 4 MW | 100000
100000
Cooling Water
Cooling Tower |  | 100000
100000
Instrument Air
Instrument Air Comp | 1 | 25000
Piping |  | 10000
35000
Total |  |  | 235000 | 235000 | 235000 | 235000 | 235000

## Civil
CIVIL
|  |  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
Indoor
Comp Building (with trench) | 60 X 45 | 300000
Cold Box room | 60 X 45 | 300000
Controls room | 20 X 20 | 100000
Test area (with trench) | 90 X 45 | 400000
Outdoor
Ghe Tank form | 45 X 45 | 15000
Ln2 Dewar | 15 X 45 | 10000
Lhe Dewar | 10 d | 5000
Oilremoval | 15 X 20 | 5000
Cooling Tower | 45 X 45 | 15000
Substation | 10 X 20 | 5000
Total |  | 1155000 | 1155000 | 1155000 | 1055000 | 1055000

## Controls
Controls
|  | Option-1A | Option-1B | Option-2A | Option-2B | Notes
Total Cost ($)
Control system | 300000
Equip. Total | 300000 | 300000 | 300000 | 300000 | 300000

## Engineering
Engineering
Notes
Fermi
Linde
Jlab

## Installation
Installation
Notes
Fermi
Linde
Jlab

## Comissioning
Comissioning
Notes
Fermi
Linde
Jlab

## Numbering
Recomended CRYOGENIC SYSTEMS NUMBERING |  |  |  | Index
SMTF
00000-09999 |  |  |  | General Block and Flow Diagrams | GFD
10000-19999 |  |  |  | Helium Gas Storage | HGS
20000-29999 |  |  |  | Main Compressor System | MCS
30000-39999 |  |  |  | Main Cold Box | MCB
40000-49999 |  |  |  | Subatmospheric Cold Box | SCB
50000-59999 |  |  |  | Distribution System | DS
| 50000-53999 |  |  | Distribution Box | DBX
| 54000-56999 |  |  | CM_Distribution | CMD
| 57000-58999 |  |  | Test DewarDistribution | TDD
60000-69999 |  |  |  | Spare
70000-79999 |  |  |  | Helium Purifiers General | HPG
| 70000-73999 |  |  | Helium Purifier System | HPS
80000-89999 |  |  |  | Utility Systems | UTS
90000-99999 |  |  |  | Spare
00000-09999 |  |  |  | General Block and Flow Diagrams (GFD) |  |  |  | Remarks
10000-19999 |  |  |  | Helium Gas Storage (HGS)
|  | 10000-10999 |  | Flow Diagrams
|  | 11000-11999 |  | Helium Gas Tanks
|  | 12000-12999 |  | Helium Purity Monitors
|  | 13000-19999 |  | Spare
20000-29999 |  |  |  | Compressor System (CMP) |  |  |  | Remarks
| 20000-23999 |  |  | Main Compressor System (MCS)
|  | 20000-20999 |  | Oil Removal & Gas Management
|  | 21000-21999 |  | First Stage Helium Compressors
|  |  | 21000-21099 | Flow Diagrams
|  |  | 21100-21199 | CMP211
|  |  | 21200-21299 | CMP212
|  |  | 21400-21999 | Spare
|  | 22000-22999 |  | Second Stage Helium Compressors
|  |  | 22000-22099 | Flow Diagrams
|  |  | 22100-22199 | CMP221
|  |  | 22200-22299 | CMP222
|  |  | 22400-22999 | Spare
| 24000-29999 |  |  | Spare
30000-39999 |  |  |  | 4.5K Cold Box Systems (CBX) |  |  |  | Remarks
| 30000-33999 |  |  | Main Cold Boxs General
|  | 31000-31999 |  | CHL 4.5K Main Cold Box (MCB)
|  |  | 31000-31099 | General
|  |  | 31100-31199 | Low Pressure
|  |  | 31200-31299 | Medium Pressure
|  |  | 31300-31399 | High Pressure
|  |  | 31400-31499 | Nitrogen
|  |  | 31500-31599 | Cooldown/Regeneration
|  |  | 31600-31699 | Spare
|  |  | 31700-31799 | Instrument Air
|  |  | 31800-31899 | Cooling Water
|  |  | 31900-31999 | Vacuum
|  | 32000-33999 |  | Spare
| 34000-35999 |  |  | 4.5 K Lhe Storage System General
|  | 34000-34999 |  | 4.5 K Helium Dewar System (LHeD)
|  |  | 34000-34099 | General
|  |  | 34100-34199 | T0 2.1 K CBX
|  |  | 34200-34299 | T0/From 4.5 K CBX
|  |  | 34300-34399 | T0 Cooldown
|  |  | 34400-34999 | Spare
|  | 35000-35999 |  | Spare
| 36000-39999 |  |  | Spare
40000-49999 |  |  |  | Sub_Atmospheric Systems |  |  |  | Remarks
| 40000-42999 |  |  | Cold Compressor System
|  | 41000-41999 |  | 2.1K Subatmospheric Cold Box (SCB)
|  |  | 41000-41099 | General
|  |  | 41100-41199 | Low Pressure
|  |  | 41200-41399 | Spare
|  |  | 41400-41499 | Nitrogen
|  |  | 41500-41599 | Cooldown/Regeneration
|  |  | 41600-41699 | Spare
|  |  | 41700-41799 | Instrument Air
|  |  | 41800-41899 | Cooling Water
|  |  | 41900-41999 | Vacuum
|  | 42000-42999 |  | Spare
| 43000-45999 |  |  | Spare
| 46000-48999 |  |  | Process (Kinney) Vacuum System (PVS)
|  | 46000-46099 |  | Flow Diagrams
|  | 46100-46999 |  | Oil Removal & Gas Management
|  | 47000-47999 |  | PVS1 (Kinney-1)
|  |  | 47000-47099 | Flow Diagrams
|  |  | 47100-47199 | Blower
|  |  | 47200-47299 | Ring Pump
|  |  | 47300-47399 | Oil Removal Tank & Oil Lines
|  |  | 47400-47699 | Spare
|  |  | 47700-47799 | Instrument Air
|  |  | 47800-47899 | Cooling Water
|  |  | 47900-47999 | Vacuum
|  | 48000-48999 |  | PVS2 (Kinney-2)
|  |  | 48000-48099 | Flow Diagrams
|  |  | 48100-48199 | Blower
|  |  | 48200-48299 | Ring Pump
|  |  | 48300-48399 | Oil Removal Tank & Oil Lines
|  |  | 48400-48699 | Spare
|  |  | 48700-48799 | Instrument Air
|  |  | 48800-48899 | Cooling Water
|  |  | 48900-48999 | Vacuum
| 49000-49999 |  |  | Spare
50000-59999 |  |  |  | Load Distribution System (LDS) |  |  |  | Remarks
|  | 50000-50999 |  | General to Over All System
|  | 51000-51999 |  | Primary Supply
|  |  | 51000-51099 | Primary Supply gen
|  |  | 51100-51199 | CM
|  |  | 51200-51299 | Test Dewars
|  |  | 51300-51999 | Spare
|  | 52000-52999 |  | Primary Return
|  |  | 52000-52999 | Primary Return gen
|  |  | 52100-52199 | CM
|  |  | 52200-52299 | Test Dewars
|  |  | 52300-52999 | Spare
|  | 53000-53999 |  | Shield Supply
|  |  | 53000-53099 | Shield Supply gen
|  |  | 53100-53199 | CM
|  |  | 53200-53299 | Test Dewars
|  |  | 53300-53999 | Spare
|  | 54000-54999 |  | Shield Return
|  |  | 54000-54099 | Shield Return gen
|  |  | 54100-54199 | CM
|  |  | 54200-54299 | Test Dewars
|  |  | 54300-54399 | Spare
|  | 55000-55999 |  | 3 ATM Supply
|  |  | 55000-55099 | 3 Atm Sup Gen
|  |  | 55100-55199 | 3 Atm Sup CM
|  |  | 55200-53999 | 3 Atm Sup Test Dewars
|  |  | 55300-55999 | Spare
|  | 56000-56999 |  | Cooldown
|  |  | 56000-56099 | CD gen
|  |  | 56100-56199 | CD_CM
|  |  | 56200-56299 | CD_Test Dewars
|  |  | 56500-56599 | Spare
|  |  | 56600-56999 | Spare
|  | 57000-58999 |  | Spare
|  | 59000-59999 |  | Vacuum System |  |  |  | Remarks
|  |  | 59000-59099 | Guard Vac gen
|  |  | 59100-59199 | Guard Vac CM
|  |  | 59200-59299 | Guard Vac Test Dewars
|  |  | 59300-59299 | Spare
|  |  | 59600-59599 | Spare
60000-69999 |  |  |  | Sp[are |  |  |  | Remarks
70000-79999 |  |  |  | Helium Purifiers General (HPG) |  |  |  | Remarks
| 70000-73999 |  |  | Helium Purifier System (HPS)
|  | 70000-70999 | 70000-70099 | General Flow Diagram
|  |  | 70100-70199 | Clean-Up from Storage
|  |  | 70200-70299 | Clean-Up from CHL Compressor
|  |  | 70300-70399 | Clean-Up from CHL MCB
|  |  | 70400-70499 | Clean-Up from CHL 2.1K CB
|  |  | 70600-70699 | Clean-Up from CTF
|  | 71000-71999 |  | Recovery Compressors
|  |  | 71000-71099 | Common to Recovery Compressors
|  |  | 71100-71199 | Recovery Compressor -1
|  |  | 71200-71299 | Recovery Compressor -2
|  |  | 71300-71399 | Recovery Compressor -3 (Future)
|  | 72000-72999 |  | Purifier Molsieve (Dryer) System | Common | Bed -1 | Bed -2
|  |  | 72000-72099 | General
|  |  | 72100-72199 | Not Used
|  |  | 72200-72299 | Not Used
|  |  | 72300-72399 | High Pressure | 72300-72309 | 72310-72319 | 72320-72329
|  |  | 72400-72499 | Nitrogen | 72400-72409 | 72410-72419 | 72420-72429
|  |  | 72500-72599 | Cooldown | 72500-72509 | 72510-72519 | 72520-72529
|  |  | 72600-72699 | Warmup | 72600-72609 | 72610-72619 | 72620-72629
|  |  | 72700-72799 | Instrument Air System | 72700-72709 | 72710-72719 | 72720-72729
|  |  | 72800-72899 | Cooling Water System | 72800-72809 | 72810-72819 | 72820-72829
|  |  | 72900-72999 | Vacuum System | 72900-72909 | 72910-72919 | 72920-72929
|  | 73000-73999 |  | Purifier Cold Box System | Common | Bed -1 | Bed -2
|  |  | 73000-73099 | General
|  |  | 73100-73199 | Not Used
|  |  | 73200-73299 | Not Used
|  |  | 73300-73399 | High Pressure | 73300-73309 | 73310-73319 | 73320-73329
|  |  | 73400-73499 | Nitrogen | 73400-73409 | 73410-73419 | 73420-73429
|  |  | 73500-73599 | Cooldown | 73500-73509 | 73510-73519 | 73520-73529
|  |  | 73600-73699 | Warmup | 73600-73609 | 73610-73619 | 73620-73629
|  |  | 73700-73799 | Instrument Air System | 73700-73709 | 73710-73719 | 73720-73729
|  |  | 73800-73899 | Cooling Water System | 73800-73809 | 73810-73819 | 73820-73829
|  |  | 73900-73999 | Vacuum System | 73900-73909 | 73910-73919 | 73920-73929
| 74000-79999 |  |  | Spare
80000-89999 |  |  |  | Utility Systems (UTS) |  |  |  | Remarks
|  |  | 80000-80999 | Flow Diagrams
|  |  | 81000-81999 | Spare
|  |  | 82000-82999 | Spare
|  |  | 83000-83999 | 3 ATM He
|  |  | 84000-84999 | Oil System
|  |  | 85000-85999 | Instrument Air System
|  |  | 86000-86999 | Cooling Water System
|  |  | 87000-87999 | GN2 Distribution System
|  |  | 88000-88999 | LN2 Dewar and Distribution System
|  |  | 89000-89999 | Vacuum System
|  |  |  | General | 89000-89099
|  |  |  | Guard Vacuum #1 | 89100-89199
|  |  |  | Guard Vacuum #2 | 89200-89299
|  |  |  | SCB Roughing/Backing Pump | 89300-89399
|  |  |  | Spare | 89400-89499
|  |  |  | Vac. Pump Cart for MCB 80K & 20Kbeds | 89500-89599
|  |  |  | Vac. Pump Cart for Purifier Molsieve Beds | 89600-89699
|  |  |  | Vac. Pump Cart for Purifier 80K Beds | 89700-89799
90000-99999 |  |  |  | Spare