SPILL PREVENTION, CONTROL, AND COUNTERMEASURE PLAN

National Weather Service

Newport Forecast Office

533 Roberts Road

Newport, NC  28570

MANAGEMENT APPROVAL

This spill prevention, control, and countermeasure (SPCC) plan was carefully thought out, prepared in accordance with good engineering practices, and has the full approval of National Weather Service management at a level with the authority to commit the necessary resources for its implementation.  In accordance with Title 40 of the Code of Federal Regulations (40 CFR), Part 112.5 this SPCC plan will be updated within 1 year of a change in facility design, construction, operation, or maintenance that materially affects the facility’s potential for discharge of oil to navigable waters or adjoining shorelines.  This plan will be implemented as described herein and will be reviewed and evaluated at least every 3 years to include more effective prevention and control technologies, if available.  This current plan replaces plans reviewed and/or revised every 3 years since the facility began operations in 1993.

Robert Brashears / Electronic Technician

Printed Name and Title of Responsible Manager

Signature of Responsible Manager and Date Signed

PLAN CERTIFICATION

I hereby certify that I have examined the facility, and being familiar with the provisions of 40 CFR Part 112, I attest that this SPCC plan has been prepared in accordance with good engineering practices.

| Printed Name of Registered Engineer |
| --- |
| Signature of Registered Engineer and Date Signed |
| Registration No. | State |

CONTENTS

Page

A.	GENERAL FACILITY INFORMATION	1

B.	SCHEDULE FOR IMPLEMENTATION - 112.7	1

C.	SPILL HISTORY - 112.7(a)	2

D.	POTENTIAL SPILLS, PREDICTION, AND CONTROL	2

1.	Facility Description	2

2.	Prediction of Potential Spills - 112.7(b)	2

3.	Spill Controls - 112.7(c)	3

E.	FACILITY DRAINAGE - 112.7(e)(1)	3

F.	BULK STORAGE TANKS - 112.7(e)(2)	4

G.	FACILITY TRANSFER OPERATIONS, PUMPING, AND IN-PLANT PROCESS - 112.7(e)(3)	4

I.	INSPECTIONS AND RECORDS - 112.7(e)(8)	5

J.	SECURITY - 112.7(e)(9)	5

K.	PERSONNEL, TRAINING, AND SPILL PREVENTION PROCEDURES - 112.7(e)(10)	5

L.	SUBSTANTIAL HARM CRITERIA EVALAUATION – 112.20 (f)(1)	5

M.	SPILL COUNTERMEASURES AND REPORTING	6

1.	Spill Countermeasures	6

2.	Spill Notification Procedures	6

Appendix

A	INSPECTION FORM

B	TRAINING OUTLINE AND COPY OF TITLE 40 OF THE CODE OF FEDERAL REGULATIONS Section 112.1-112.20-Oil Pollution Prevention

C	SPILL NOTIFICATION FORM

FIGURES

Figure	Page

1	SITE LOCATION	8

2	FACILITY LAYOUT AND SPILL PATH	9

TABLES

Table	Page

1	POTENTIAL SPILL SOURCES AND VOLUMES	3

2	DESCRIPTIVE INVENTORY OF BULK STORAGE TANKS	4

A.	GENERAL FACILITY INFORMATION

Name:	National Weather Service (NWS), Newport Forecast Office (also known as NWS Moorehead City Weather Forecast Office [WFO])

Type:	National Weather Service forecast office and a Radar Data Acquisition (RDA) site containing two emergency backup power generators and associated aboveground storage tanks (AST).

Location:	533 Roberts Road

Newport, Carteret County, North Carolina 28570

Name and Address of Owner:

National Weather Service

Eastern Region

251 Fuller Road

Albany, New York  12203

Designated Person Responsible for Spill Prevention at this Facility - 112.7(e)(10)

Environmental Coordinator:  Robert Brashears, Electronic Technician

Office:		(252) 223-5007

Alternate:	(252) 223-2328

Date of Initial Operation:

1993

B.	SCHEDULE FOR IMPLEMENTATION - 112.7

The following physical changes will materially affect the facility's potential to discharge oil and will be made within six months of the Responsible Manager's signature per 40 CFR 112.  Within 6 months of the implementation of the following physical changes, the SPCC plan will be amended to reflect the changes, and a Professional Engineer will certify amendments in accordance with 40 CFR Part 112.5(c).  In addition, various improvements will be made to enhance spill prevention practices at this facility.  The following will be implemented:

1.	A fence with a locking gate shall be constructed around the AST to prevent vandalism.

- Diesel fuel oil procedures to be followed before and after unloading will be implemented as described in Section H.  The facility will acquire improved signage (current signage is partially unreadable).  An area shall be constructed to provide containment for the largest compartment of the tank truck unloading fuel at both the WFO and the RDA site.

- The high-level alarm on the AST should be fixed so it operates properly and sounds at 85 percent capacity.  In addition a high-high level alarm or automatic shut-off valve on the fill pipe shall be set to sound or stop the flow into the AST at 90 percent capacity.

4.	A formal inspection program for the ASTs, associated piping, foundations, secondary containment systems, and unloading rack area will be implemented as described in Section F.  Appendix A provides an inspection form to document inspection activities.

5.	A formal training program will be implemented as described in Section K.  Appendix B provides a training program outline.

6.	The facility intends to purchase and store spill response supplies to contain and quickly remove small leaks or spills that occur.

7.	As a good management practice, spill cleanup contractors will be researched and identified to assist with cleanup efforts in the event a spill occurs, and additional spill response supplies will be acquired as described in Section D.3.

C.	SPILL HISTORY - 112.7(a)

This facility has not had a reportable spill.  Should this facility have a reportable oil spill greater than 1,000 gallons in a single spill event or two reportable spills within any 12-month period, this SPCC plan and a report as outlined in 40 CFR Part 112.4 will be submitted to U.S. Environmental Protection Agency Regional Administrator and the state agency in charge of water pollution control activities within 60 days of the incident(s).

D.	POTENTIAL SPILLS, PREDICTION, AND CONTROL

1.	Facility Description

The facility is located inside the city limits of Newport, North Carolina.  It is located approximately 1.5 miles southwest of the town square (Figure 1).  Figure 2 shows the layout of the facility, including the location of the 2,000-gallon AST and adjacent generator shed and the RDA site containing the two day tanks and an emergency backup generator.

A local commercial supplier periodically fills the ASTs.  The estimated annual fuel usage at the facility is approximately 3,000 to 4,000 gallons.  This estimate is based on testing the generator once per week for 60 minutes as well as use during inclement weather.  Fuel consumption would increase based on the frequency and duration of any power outages.

2.	Prediction of Potential Spills - 112.7(b)

The AST is located on a concrete pad at the facility.  If secondary containment were somehow breached, the diesel would flow to the south or southwest, toward a wetland area (See Figure 2).  The two day tanks are located inside the generator building at the RDA site.  Small spills or leaks emanating from these tanks would be contained within the generator building (capacity approximately 750 gallons).  If the containment were somehow breached, flow would be toward the north or northwest, toward a wetland area (See Figure 2).

The most probable cause for spills from the AST and from the two day tanks is from overfilling.  Table 1 summarizes the potential failure types, potential spill volumes, estimated rates, and direction of spill flow.

TABLE 1

POTENTIAL SPILL SOURCES AND VOLUMES

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| AST | Overfilling | 50 to 60 | 50 to 60 gallons per minute | South or Southwest | Operational procedures are in place to prevent overfilling. |
|  | Structural failure | 2,000 | Gradually to instantaneously, depending on size of hole | South or Southwest | Failure of both the primary shell and secondary concrete structure is a low probability event. |
| RDA Day Tanks | Overfilling | 50 to 60 | 50 to 60 gallons per minute | North or Northwest | Operational procedures are in place to prevent overfilling. |
|  | Structural failure | 2 X 250 | Gradually to instantaneously, depending on size of hole | North or Northwest | Volume inside generator building greater that total capacity |

3.	Spill Controls - 112.7(c)

Aside from those items mentioned in Section B, appropriate containment and diversionary structures and equipment to prevent discharged oil from reaching navigable waters have been installed for the AST.  The AST is enclosed in Convault®-type container.  The steel tank is covered with Styrofoam® for insulation then entirely wrapped in 30 mil high density polyethylene.  The is then encased in a concrete containment structure.  A “dipstick” is used to gauge fuel levels in the AST, and a high level/low level audible alarm on the float-type level gauge audibly indicates the fuel level.  The low- and high-level alarms are audible outside and in the control room.  The AST is bolted to its concrete foundation.

The two day tanks are totally enclosed inside the generator shed, protected from the elements.  This facility has installed equipment and/or structures to prevent discharged oil from reaching navigable waters per 40 CFR Part 112.7(c)(1)(i); therefore, an oil spill contingency plan that follows 40 CFR Part 109 is not required.  In addition, as explained in Section B., the facility intends to purchase and store spill response supplies (for example, 100 pounds of granular oil absorbent, oil absorbent pads, a broom, and a shovel) to contain and quickly remove small leaks or spills that occur . A local oil spill cleanup contractor(s) will be identified to respond in case of a spill that exceeds the facility’s management ability.

E.	FACILITY DRAINAGE - 112.7(e)(1)

The AST is completely encased in concrete; therefore, no rainwater is expected to accumulate in the containment area.

Facility drainage of storm water in the areas surrounding the AST flows to the adjacent property via sheet flow to the wetlands to the south.  Good management practices including inspections, personnel training, and readily available spill response supplies are used to prevent oil from reaching navigable waters in the event of equipment failure or human error at the facility.  Facility drainage is illustrated in Figure 2.

F.	BULK STORAGE TANKS - 112.7(e)(2)

Both the AST and the day tanks are constructed of steel and are compatible with the product stored.  The interstitial space of the double-walled, rectangular welded AST provides an additional 10 percent (200 gallons) of sufficiently impervious secondary containment.  The floor of the generator shed provides adequate secondary containment for the two day tanks.

All three tanks and their foundations are visually integrity tested through monthly inspections for signs of deterioration and leaks that might cause a spill.  The accumulation of oil in the interstitial space of the AST is also inspected.  Documented records of these inspections are kept on site for 3 years.  Copies of the inspection form are provided in Appendix A.

There are no buried, partially buried, internally heated, mobile, or portable tanks on this facility.

The AST is engineered with low and high-level audible alarms.  As backup, the AST is stick-inventoried before unloading occurs, and operators continuously monitor unloading operations.  Any leak is investigated to determine the cause of the leak, and corrective actions are taken, as appropriate.  Table 2 presents a descriptive inventory of the bulk fuel tanks at the facility.

TABLE 2

DESCRIPTIVE INVENTORY BULK FUEL STORAGE TANKS

| Tank | Product Stored | Nominal Capacity (Gallons) | Tank Type/Year | Failure/Cause |
| --- | --- | --- | --- | --- |
| AST | Diesel fuel oil | 2,000 | Steel/1993 | Not applicable |
| RDA Day Tanks | Diesel fuel oil | 2 x 250 | Steel/1993 | Not applicable |

G.	FACILITY TRANSFER OPERATIONS, PUMPING, AND IN-PLANT PROCESS - 112.7(e)(3)

All piping between the day tanks and their respective generators is aboveground.  An overhead double-walled supply pipe connects the AST to the generator day tanks.  This piping is completely encased in 4-inch polyvinyl chloride piping.  The piping at the RDA unit is completely contained in the generator room.  There is no underground piping on the facility.

H.	FACILITY TANK TRUCK UNLOADING RACK - 112.7(e)(4)

Facility unloading procedures meet the minimum requirements and regulations established by the U.S. Department of Transportation (DOT), Title 49 of the CFR Part 177.834, to include the following:

1.	No smoking while unloading.

2.	The vehicle handbrake is set.

3.	Unloading material will be attended by a qualified person at all times.

4.	All valves and other closures are closed and free of leaks before the departure of unloading vehicles.

The unloading rack area is composed of a flat concrete pad with no berm to provide containment in the event of the failure of the fuel tank truck.  As explained in Section B.2, containment will be provided per 40 CFR Part 112.7(e)(4)(ii).

Signage will be acquired and posted, as described in Section B.2., to identify actions to be taken before and after unloading.  Actions include satisfying DOT requirements, disconnecting the transfer lines, and inspecting all drains and outlets on the tanker truck for leakage.  Monthly inspections will include inspecting the rack area for cracks in the pavement.

Note:  Since this facility is not an oil production, oil drilling, or workover facility, 40 CFR Parts 112.7(e)(5), (6), and (7) do not apply.

I.	INSPECTIONS AND RECORDS - 112.7(e)(8)

A formal inspection program will be implemented as described in Section B.3.  Documented inspection records will be maintained in the facility’s main office, for a minimum of 3 years in accordance with the written procedures discussed in Section F.  Appendix A contains a copy of the inspection form.

J.	SECURITY - 112.7(e)(9)

A 6-foot-high chain-link security fence surrounds the RDA units and has a locked gate.  The day tanks are located within a shed that provides additional security.  There is currently no fence surrounding the AST.  As explained in Section B.1, a fence with a locking gate shall be constructed around the AST.  The area around all the tanks are well lit to facilitate the detection of leaks and spills during night-time hours and to deter vandalism.

K.	PERSONNEL, TRAINING, AND SPILL PREVENTION PROCEDURES - 112.7(e)(10)

A formal training program will be established as discussed in Section B.4.  All facility personnel responsible for implementing the SPCC plan will be properly instructed in the operation and maintenance of all equipment and supplies used to prevent oil discharges as well as the applicable spill prevention regulations.  Refresher training will be provided on an annual basis or whenever physical or procedural changes occur at the facility.  Training will highlight and describe known spill events or failures, malfunctioning components, and recently developed precautionary measures.  The person accountable for the facility spill prevention and for training personnel is identified in Section A.6.  Appendix B contains a training program outline.

L.	SUBSTANTIAL HARM CRITERIA EVALAUATION – 112.20 (f)(1)

This facility is not required to have a facility response plan under 40 CFR Part 112.20 since it does not:

- Transfer oil over water from vessels and have a total oil storage capacity of greater than or equal to 42,000 gallons, or

- Have a total storage capacity over 1 million gallons.

M.	SPILL COUNTERMEASURES AND REPORTING

The primary emphasis of this SPCC plan is prevention.  This section presents countermeasures to contain, clean up, and mitigate the effects of an oil spill that impacts navigable waters or adjacent shorelines.  (This does not constitute a contingency plan under 40 CFR Part 109, nor is such a plan required for this facility.)  Should a spill occur that impacts navigable waters or adjacent shorelines, however, the following measures will be implemented.

1.	Spill Countermeasures

A spill containment and cleanup activity will never take precedence over the safety of personnel.  No countermeasure activities will be undertaken until conditions are safe for workers.  The following general procedures should be implemented as countermeasures:

a.	Account for all personnel, and ensure their safety.

b.	Divert flow away from drainage channels, and cover storm drain corner with contents of spill kit.

c.	Attempt to seal or stop leak.

d.	Acquire necessary resources to contain and clean up all oil-contaminated areas.

e.	Make all necessary notifications as described in the following text.

2.	Spill Notification Procedures

This section discusses the reporting procedures for spills of diesel fuel at the facility.  The people and organizations that are notified vary based on the quantity of the spill, whether it reaches navigable waters or adjoining shorelines, and the frequency of spills.

A spill reporting form that requests the information to be reported to all agencies in written form (to the extent known) is included in Appendix D.  Copies of the completed form should be sent to the NWS Environmental Compliance Officer and the National Oceanic and Atmospheric Administration (NOAA) Western Regional Compliance Officer (see following section).

a.	General Notification Procedures For All Spills

The responsible person or designee is directly charged with reporting all oil spills that result from facility operations as follows:

- First, call 515-3333 (area code 919) if there is an immediate emergency, to access University Public Safety.

- Next, notify the appropriate persons within the NWS:

- Mike Jacob, (301) 713-1838 Ext. 165, NWS Environmental Compliance Officer.

- Olga Kebis, (301) 713-1838 Ext. 173, NWS Safety Officer

- Frank Bain (817) 978-2367 Ext. 139, NWS Eastern Regional Environmental/Safety Coordinator

- Lynnette Ansell, (757) 441-6298, NOAA Eastern Regional Compliance Officer

The form in Appendix C should be used to document notifications made after a spill has been discovered.

b.	Federal Notifications

The Federal Clean Water Act, as described in 40 CFR Part 110.6, requires notifying the U.S. Environmental Protection Agency (EPA) National Response Center (or the U.S. Coast Guard [USCG]) as soon as anyone has knowledge of any discharges of oil in quantities that “may be harmful.”  40 CFR Part 110.3 defines “may be harmful” as a discharge for which one of the following applies:

- Violates applicable water quality standards

- Causes a film or sheen upon or discoloration of the surface of the water or adjoining shorelines or cause a sludge or emulsion to be deposited beneath the surface of the water or upon adjoining shorelines

If either of these criteria is met, contact the following:

- The National Response Center (EPA and USCG):  (800) 424-8802.

Under the SPCC regulations, spill information listed in 40 CFR 112.4(a) must be reported to the regional EPA office within 60 days if either of the following occurs:

- A discharge of more than 1,000 gallons of oil into or upon navigable waters or adjoining shorelines in a single event

- Two spill events that cause visible sheens upon navigable waters or adjoining shorelines within any 12-month period

Diesel fuel is not listed as a hazardous substance under the Comprehensive Environmental Response, Compensation, and Liability Act (CERCLA); therefore, no other notification to the EPA is required for discharges of diesel fuel other than those listed previously.

c.	State Notification

The North Carolina Division of Emergency Management require notification if:

- Any quantity is spilled to a surface water, or

- Any spill to land exceeding 25 gallons.

These spills must be reported to the North Carolina Department of Crime Control and Public Safety, Division of Emergency Management at 800-858-0368.

- Cleanup Contractor Notification

An emergency response contractor should also be notified to assist with the cleanup, if necessary.  Since the facility is located on the campus of North Carolina State University, the following number should be called to assist with as spill cleanup:

  - {FACILITY TO INSERT APPROPRIATE TELEPHONE NUMBER}

FIGURE 1 - SITE LOCATION

FIGURE 2 - SITE LAYOUT

APPENDIX A

INSPECTION FORM

APPENDIX A

INSPECTION FORM

| MONTHLY INSPECTION CHECKLIST |
| --- |
| Date of Inspection: | Inspector: |
| TANKS/FOUNDATIONS | YES | NO | COMMENTS |
| 1. Drip marks or stains on outside of tanks? |  |  |  |
| 2. Oil on the ground around tanks? |  |  |  |
| 3. Indications of corrosion (e.g., paint peeling, rust)? |  |  |  |
| 4. Raised spots or dents on the surface of the tanks? |  |  |  |
| 5. All vents clear to properly operate? |  |  |  |
| 6. Fuel gauge and alarms working properly? |  |  |  |
| 7. Foundation appear shifted or settled? |  |  |  |
| SECONDARY CONTAINMENT | YES | NO | COMMENTS |
| 8. Indications of corrosion (e.g., paint peeling, rust)? |  |  |  |
| 9. Presence of spilled or leaked material (standing liquid)? |  |  |  |
| 10. Rainwater present? (If yes, remove and inspect for sheen) |  |  |  |
| PIPING | YES | NO | COMMENTS |
| 11. Oil under aboveground piping, hoses, fittings, or valves? |  |  |  |
| 12. All piping, hoses, fittings, and valves working properly? |  |  |  |

| UNLOADING RACK AREA | YES | NO | COMMENTS |
| --- | --- | --- | --- |
| 13. Warning signs properly posted and legible? |  |  |  |
| 14. Visible cracks in the pavement? |  |  |  |
| SECURITY/SAFETY/SPILL RESPONSE | YES | NO | COMMENTS |
| 15. Security fencing/gate in good condition? |  |  |  |
| 16. Lights working properly to observe a spill during night? |  |  |  |
| 17. Spill kits easily accessible and complete? |  |  |  |
| Corrective Actions Required: |

APPENDIX B

TRAINING OUTLINE AND COPY OF TITLE 40 OF THE CODE OF FEDERAL REGULATIONS Section 112.1-112.20-Oil Pollution Prevention

APPENDIX B

OUTLINE FOR SPILL PREVENTION, CONTROL, AND COUNTERMEASURES TRAINING

I.	INITIAL TRAINING.  Initial training shall be provided for all facility personnel within their first week of employment to familiarize employees with the following information:

A.	Summary of spill prevention regulations (Title 40 of the Code of Federal Regulations Part 112)

B.	Purpose and application of system elements

1.	Tanks and associated piping

2.	Unloading rack area

3.	Accessory equipment (e.g., generator and pumps)

4.	Gauges and alarms

5.	Spill supplies

C.	Spill prevention

1.	Potential spill sources

2.	Procedures to prevent spills

3.	Inspections and documentation

D.	Spill control

1.	Spill flow direction and impact on navigable waters

2.	Secondary containment systems

3.	Overflow protection and leak detection systems

4.	Alarm recognition and response

E.	Spill countermeasures

1.	Personnel accountability

2.	Spill supplies and equipment use

3.	Methods to stop and seal leaks

4.	Emergency phone numbers and notifications

II.	REFRESHER TRAINING.  Annual refresher training shall be provided to highlight and describe at least the following:

A.	Known spill events or failures

B.	Malfunctioning components

C.	Recently developed precautionary measures

III.	ON-GOING TRAINING.  On-the-job training or briefings shall be provided throughout the year whenever physical or procedural changes occur at the facility.

ATTACHMENT

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS Section 112.1  - 112.20

Oil Pollution Prevention

APPENDIX C

SPILL REPORTING FORM

APPENDIX C

SPILL REPORTING FORM

| GENERAL |
| --- |
| Name of Facility: National Weather Service, Newport Forecast Office |
| Organization: Federal Government |
| Address: 533 Roberts Road, Newport, NC 28570 |
| REPORTING PARTY |
| Report Completed By: |
| Position: |
| Phone Number: |
| SPILL INFORMATION |
| Date: | Time: AM / PM |
| Substance spilled: Diesel Fuel Oil | Estimated Quantity: |
| Source and Cause: |
| OUTSIDE NOTIFICATIONS |
| Agencies | Recorder at Outside Agency | Date/Time |
| NRC: (800) 424-8802 |  |  |
| DESCRIPTION OF ENVIRONMENTAL DAMAGE |
| CLEANUP ACTION(S) TAKEN |
| CORRECTIVE ACTION(S) TO PREVENT FUTURE SPILLS |

Note:  All information must be filled in.  If something is unknown, write “unknown.”