## 25F nomo
Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 044
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6649.518
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -212.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 79.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | -68.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1010.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 79.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2742.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 718.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3191.41 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 849.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 3050.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1010.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | -68.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2429.5 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 849.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2598.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2598.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2742.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3168.95 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3163.78 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2977.79 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3168.95 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -212.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3191.41 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 718.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2624.82 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2429.5 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2977.79 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3163.78 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3050.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2624.82 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 044
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6317.5127
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 149.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 466.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 313.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1363.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 466.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3044.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1065.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3099.23 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1200.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2963.03 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1363.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 313.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2735.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1200.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2906.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2906.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3044.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3081.39 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3075.48 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2733.67 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3081.39 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 149.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3099.23 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1065.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2388.75 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2735.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2733.67 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3075.48 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2963.03 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2388.75 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 044
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6031.2153
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -39.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 264.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 118.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1104.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 264.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2811.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 829.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3042.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 946.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2896.94 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1104.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 118.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2520.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 946.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2675.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2675.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2811.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3028.45 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3017.65 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2632.55 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3028.45 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -39.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3042.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 829.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2260.31 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2520.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2632.55 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3017.65 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2896.94 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2260.31 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 044
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4962.1587
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1329.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1633.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1480.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2418.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1633.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3245.39 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2141.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2839.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2274.65 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2282.3 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 2418.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1480.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3225.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2274.65 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3236.22 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3236.22 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3245.39 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2828.99 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2525.38 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2129.46 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2828.99 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1329.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2839.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2141.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 1785.16 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3225.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2129.46 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2525.38 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2282.3 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1785.16 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 044
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4628.374
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1594.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1932.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1756.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2682.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1932.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3183.9 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2392.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2481.22 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 2555.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1893.8 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 2682.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 1756.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3140.18 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2555.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3168.34 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3168.34 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3183.9 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2694.9 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2369.21 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1929.07 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2694.9 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1594.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2481.22 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2392.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 1602.12 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3140.18 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1929.07 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2369.21 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1893.8 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1602.12 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
G0 | -212.81 | 149.11 | -39.15 | 1329.39 | 1594.68
G1 | -68.11 | 313.39 | 118.8 | 1480.13 | 1756.55 | Season/Year: | WINTER 2009
G2 | 79.56 | 466.16 | 264.82 | 1633.29 | 1932.5 | Direction: | North-to-South (NS)
G3 | 718.5 | 1065.71 | 829.47 | 2141.75 | 2392.16 | Case Loads: | Heavy Loads
G4 | 849.36 | 1200.23 | 946.76 | 2274.65 | 2555.96 | Outage: | 044
G5 | 1010.12 | 1363.13 | 1104.82 | 2418.94 | 2682.92 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2429.5 | 2735.32 | 2520.11 | 3225.01 | 3140.18 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2598.22 | 2906.12 | 2675.05 | 3236.22 | 3168.34 | Study Person: | FRP9899
G8 | 2742.35 | 3044.84 | 2811.38 | 3245.39 | 3183.9 | Source: | 044WINTER09v2NSH(SN@100MW)
G9 | 3163.78 | 3075.48 | 3017.65 | 2525.38 | 2369.21
G10 | 3168.95 | 3081.39 | 3028.45 | 2828.99 | 2694.9
G11 | 3191.41 | 3099.23 | 3042.92 | 2839.6 | 2481.22
G12 | 2624.82 | 2388.75 | 2260.31 | 1785.16 | 1602.12
G13 | 2977.79 | 2733.67 | 2632.55 | 2129.46 | 1929.07
G14 | 3050.97 | 2963.03 | 2896.94 | 2282.3 | 1893.8
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 044 | Sno-King 500/230kV Transformer Bank #4 ***Includes Sno-King Tap sect of Echo Lake-Monroe 500kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6649.518 | -212.81 | -68.11 | 79.56 | 718.5 | 849.36 | 1010.12 | 2429.5 | 2598.22 | 2742.35 | 3163.78 | 3168.95 | 3191.41 | 2624.82 | 2977.79 | 3050.97
35F | 6317.5127 | 149.11 | 313.39 | 466.16 | 1065.71 | 1200.23 | 1363.13 | 2735.32 | 2906.12 | 3044.84 | 3075.48 | 3081.39 | 3099.23 | 2388.75 | 2733.67 | 2963.03
45F | 6031.2153 | -39.15 | 118.8 | 264.82 | 829.47 | 946.76 | 1104.82 | 2520.11 | 2675.05 | 2811.38 | 3017.65 | 3028.45 | 3042.92 | 2260.31 | 2632.55 | 2896.94
60F | 4962.1587 | 1329.39 | 1480.13 | 1633.29 | 2141.75 | 2274.65 | 2418.94 | 3225.01 | 3236.22 | 3245.39 | 2525.38 | 2828.99 | 2839.6 | 1785.16 | 2129.46 | 2282.3
70F | 4628.374 | 1594.68 | 1756.55 | 1932.5 | 2392.16 | 2555.96 | 2682.92 | 3140.18 | 3168.34 | 3183.9 | 2369.21 | 2694.9 | 2481.22 | 1602.12 | 1929.07 | 1893.8

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -213.5 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 473.01 | 472.98 | 6662.92 | -212.81 | -718.23 | FULL
G1 | -68.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 473.09 | 473.03 | 6590.59 | -68.11 | -565.37 | FULL
G2 | 78.59 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 472.72 | 472.67 | 6599.53 | 79.56 | -417.3 | FULL
G3 | 719.93 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 482.95 | 482.75 | 6655.29 | 718.5 | -141.09 | FULL
G4 | 849.28 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 482.46 | 482.35 | 6583.31 | 849.36 | 5 | FULL
G5 | 1012.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 483.14 | 482.94 | 6594.11 | 1010.12 | 162.78 | FULL
G6 | 2439.3 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -7.08 | -497.9 | -497.85 | 6680.16 | 2429.5 | 907.1 | FULL
G7 | 2608.68 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 491.4 | 491.25 | 6614.34 | 2598.22 | 1067.69 | FULL
G8 | 2755.39 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 491.58 | 491.51 | 6631.04 | 2742.35 | 1213.17 | FULL
G9 | 3179.98 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -509.36 | -508.59 | 6727.41 | 3163.78 | 1497.6 | FULL
G10 | 3185.17 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -509.83 | -509.19 | 6658.39 | 3168.95 | 1567.95 | FULL
G11 | 3206.32 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -507.32 | -506.75 | 6673.11 | 3191.41 | 1645.75 | FULL
G12 | 2634.52 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: Snohomish 230kV Bus Sect #4 | -11.79 | -746.44 | -746.36 | 6720.38 | 2624.82 | 1374.72 | FULL
G13 | 2990.94 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.64 | -757.45 | -757.41 | 6666.92 | 2977.79 | 1624.63 | FULL
G14 | 3065.8 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -511.03 | -510.43 | 6685.27 | 3050.97 | 1731.77 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 148.98 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 467.58 | 467.32 | 6327.1 | 149.11 | -457.61 | FULL
G1 | 312.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 468.22 | 468.01 | 6253.38 | 313.39 | -297.32 | FULL
G2 | 465.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 468.54 | 468.32 | 6262.93 | 466.16 | -143.69 | FULL
G3 | 1068.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 476.88 | 476.65 | 6321.81 | 1065.71 | 107.59 | FULL
G4 | 1201.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 475.92 | 476.07 | 6250.79 | 1200.23 | 258.27 | FULL
G5 | 1364.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 476.13 | 476.09 | 6263.72 | 1363.13 | 410.55 | FULL
G6 | 2747.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 483.06 | 483.02 | 6357.1 | 2735.32 | 1121.38 | FULL
G7 | 2919.8 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 483.56 | 483.32 | 6293.46 | 2906.12 | 1291.28 | FULL
G8 | 3058.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 483.37 | 483.21 | 6311.72 | 3044.84 | 1432.95 | FULL
G9 | 3090.86 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -498.87 | -498.16 | 6392.85 | 3075.48 | 1511.67 | FULL
G10 | 3095.82 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -501.64 | -500.99 | 6324.79 | 3081.39 | 1571.22 | FULL
G11 | 3114.61 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -497.54 | -496.75 | 6340.19 | 3099.23 | 1662.82 | FULL
G12 | 2395.92 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.65 | -735.43 | -735.19 | 6381.11 | 2388.75 | 1305.98 | FULL
G13 | 2745.73 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.64 | -737.32 | -737.54 | 6327.69 | 2733.67 | 1552.62 | FULL
G14 | 2977.28 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -500.26 | -499.9 | 6354.05 | 2963.03 | 1735.71 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -39.99 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 435.05 | 434.95 | 6042.63 | -39.15 | -526.75 | FULL
G1 | 117.78 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 435.41 | 435.31 | 5969.77 | 118.8 | -369.12 | FULL
G2 | 264.09 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 435.54 | 435.42 | 5979.25 | 264.82 | -219.13 | FULL
G3 | 830.4 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 441.17 | 441.14 | 6035.77 | 829.47 | 13.59 | FULL
G4 | 948.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 440.89 | 440.73 | 5965.45 | 946.76 | 160.4 | FULL
G5 | 1106.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 441.21 | 441.33 | 5977.98 | 1104.82 | 316 | FULL
G6 | 2529.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 448.2 | 448.05 | 6066.22 | 2520.11 | 1039.25 | FULL
G7 | 2684.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 447.55 | 447.54 | 6002.51 | 2675.05 | 1192.51 | FULL
G8 | 2822.5 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 447.53 | 447.64 | 6020.62 | 2811.38 | 1333.3 | FULL
G9 | 3032.55 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -491.36 | -490.94 | 6107.48 | 3017.65 | 1500.3 | FULL
G10 | 3043.94 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -491.06 | -490.57 | 6040.25 | 3028.45 | 1577.05 | FULL
G11 | 3056.17 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -490.35 | -489.98 | 6055.75 | 3042.92 | 1652.85 | FULL
G12 | 2267.74 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.65 | -715.11 | -715.08 | 6094.03 | 2260.31 | 1271.77 | FULL
G13 | 2643.07 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.65 | -717.45 | -717.43 | 6040.84 | 2632.55 | 1543.08 | FULL
G14 | 2910.2 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -490.35 | -489.76 | 6069.68 | 2896.94 | 1736.45 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1331.33 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 442.14 | 442.35 | 4957.6 | 1329.39 | 412.86 | FULL
G1 | 1482.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 443.01 | 443.08 | 4891.47 | 1480.13 | 561.34 | FULL
G2 | 1637.17 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 443.34 | 443.45 | 4907.73 | 1633.29 | 712.9 | FULL
G3 | 2148.94 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 446.16 | 445.97 | 4973.44 | 2141.75 | 900.49 | FULL
G4 | 2284.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 446.33 | 446.41 | 4909.05 | 2274.65 | 1062.07 | FULL
G5 | 2426.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 446.15 | 446.29 | 4928.1 | 2418.94 | 1197.06 | FULL
G6 | 3242.21 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -469.93 | -470.42 | 5022.34 | 3225.01 | 1602.99 | FULL
G7 | 3253.26 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -470.82 | -471.14 | 4956.97 | 3236.22 | 1663.98 | FULL
G8 | 3262.77 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -39 | -467.43 | -467.96 | 4973.83 | 3245.39 | 1749.35 | FULL
G9 | 2535.14 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.65 | -678.02 | -678.13 | 5017.69 | 2525.38 | 1443.57 | FULL
G10 | 2840.97 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.75 | -476.8 | -476.04 | 4964.47 | 2828.99 | 1671.82 | FULL
G11 | 2852.85 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.75 | -475.64 | -474.86 | 4982.2 | 2839.6 | 1732.2 | FULL
G12 | 1790.31 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.65 | -680.62 | -680.78 | 5009.65 | 1785.16 | 1216.02 | FULL
G13 | 2136.81 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.65 | -679.59 | -679.46 | 4956.16 | 2129.46 | 1467.93 | FULL
G14 | 2291.21 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 7.86 | 462.69 | 462.7 | 4981.68 | 2282.3 | 1612.79 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1598.98 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 443.18 | 443.29 | 4626.65 | 1594.68 | 609.69 | FULL
G1 | 1761.33 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 443.65 | 443.8 | 4562.14 | 1756.55 | 767.68 | FULL
G2 | 1937.93 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 445.59 | 445.54 | 4581.28 | 1932.5 | 932.77 | FULL
G3 | 2402.9 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 446.87 | 446.89 | 4646.54 | 2392.16 | 1100.53 | FULL
G4 | 2565.59 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 447.45 | 447.51 | 4584.46 | 2555.96 | 1266.67 | FULL
G5 | 2694.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.03 | 446.93 | 447.06 | 4604.94 | 2682.92 | 1397.52 | FULL
G6 | 3155.73 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.65 | -662.81 | -662.95 | 4685.22 | 3140.18 | 1610.36 | FULL
G7 | 3184.58 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.75 | -458.87 | -458.55 | 4621.92 | 3168.34 | 1694.67 | FULL
G8 | 3200.86 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.75 | -460.06 | -459.12 | 4639.63 | 3183.9 | 1772.38 | FULL
G9 | 2377.47 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.65 | -659.91 | -659.94 | 4679.22 | 2369.21 | 1416.01 | FULL
G10 | 2706.08 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.65 | -658.85 | -659.05 | 4627.39 | 2694.9 | 1655.79 | FULL
G11 | 2491.48 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 7.86 | 444.31 | 444.36 | 4640.55 | 2481.22 | 1602.95 | FULL
G12 | 1605.93 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.65 | -659.67 | -659.55 | 4671.72 | 1602.12 | 1167.19 | FULL
G13 | 1936.02 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -10.65 | -658.75 | -658.65 | 4617.91 | 1929.07 | 1409.29 | FULL
G14 | 1900.07 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 7.86 | 450.22 | 450.25 | 4636.04 | 1893.8 | 1465.81 | FULL
044WINTER09v2NSH(SN@100MW)