## 25F nomo
University-Broad Street 115kV Line (SCL) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 050
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3340.2267
Gen Level |  | Trans | Worst | Limiting |  |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [6 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3419.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G3 | 100 | 775 | 3451.3 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3428.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G6 | 260 | 775 | 3294.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3451.3 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G9 | 525 | 775 | 3018.44 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3262.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G12 | 1000 | 775 | 2594.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3268.4 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G15 | 1400 | 775 | 2447.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3294.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G2 | 100 | 465 | 3428.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2995.81 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G5 | 260 | 460 | 3268.4 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2996.94 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G8 | 525 | 460 | 2996.94 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3018.44 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G11 | 1000 | 460 | 2591.27 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2565.89 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G14 | 1400 | 460 | 2434.16 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2591.27 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G1 | 100 | 140 | 3419.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2594.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G4 | 260 | 140 | 3262.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2425.79 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G7 | 525 | 140 | 2995.81 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2434.16 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G10 | 1000 | 140 | 2565.89 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2447.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G13 | 1400 | 140 | 2425.79 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450
G1
789

## 35F nomo
University-Broad Street 115kV Line (SCL) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 050
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2662.3447
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3308.51 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3324.61 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3310.58 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3148.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3324.61 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2874.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3132.69 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2462.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3144.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2315.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3148.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3310.58 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2848.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3144.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2862.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2862.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2874.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2456.51 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2447.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2298.04 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2456.51 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3308.51 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2462.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 3132.69 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2295.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2848.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2298.04 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2447.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2315.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2295.35 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
University-Broad Street 115kV Line (SCL) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 050
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2421.4047
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3193.93 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3209.37 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3206.48 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3052.41 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3209.37 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2772.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3035.14 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2350.54 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3044.53 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2205.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3052.41 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3206.48 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2753.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3044.53 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2763.72 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2763.72 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2772.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2345.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2326.7 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2190.04 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2345.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3193.93 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2350.54 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 3035.14 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2185.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2753.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2190.04 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2326.7 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2205.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2185.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
University-Broad Street 115kV Line (SCL) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 050
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2941.0193
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3151.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3159.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3161.88 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3014.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3159.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2742.34 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2998.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2273.62 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 3011.37 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1781.43 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 3014.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 3161.88 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2719.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3011.37 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2726.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2726.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2742.34 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2308.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2293.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2160.72 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2308.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3151.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2273.62 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2998.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2139.36 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2719.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2160.72 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2293.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1781.43 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2139.36 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
University-Broad Street 115kV Line (SCL) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 050
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3281.3993
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3100.88 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2550.3 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV]
100 | 460 | 3099.89 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2314.67 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV]
100 | 775 | 2550.3 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 1993.72 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2941.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1414.67 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2944.32 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 890.44 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2314.67 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 3099.89 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2654.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2944.32 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2637.76 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2637.76 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV]
525 | 775 | 1993.72 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2041.95 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2231.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1528.93 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2041.95 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3100.88 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1414.67 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2941.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2088.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2654.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1528.93 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2231.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 890.44 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2088.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | University-Broad Street 115kV Line (SCL) (COV-CRES BYP @ COV)
G0 | 3419.46 | 3308.51 | 3193.93 | 3151.28 | 3100.88
G1 | 3428.97 | 3310.58 | 3206.48 | 3161.88 | 3099.89 | Season/Year: | WINTER 2009
G2 | 3451.3 | 3324.61 | 3209.37 | 3159.25 | 2550.3 | Direction: | North-to-South (NS)
G3 | 3262.25 | 3132.69 | 3035.14 | 2998.97 | 2941.21 | Case Loads: | Light Loads
G4 | 3268.4 | 3144.92 | 3044.53 | 3011.37 | 2944.32 | Outage: | 050
G5 | 3294.42 | 3148.63 | 3052.41 | 3014.64 | 2314.67 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2995.81 | 2848.63 | 2753.42 | 2719.2 | 2654.56 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2996.94 | 2862.35 | 2763.72 | 2726.29 | 2637.76 | Study Person: | FRP9899
G8 | 3018.44 | 2874.28 | 2772.49 | 2742.34 | 1993.72 | Source: | 050WINTER09v1NSL
G9 | 2565.89 | 2447.6 | 2326.7 | 2293.25 | 2231.47
G10 | 2591.27 | 2456.51 | 2345.02 | 2308.49 | 2041.95
G11 | 2594.75 | 2462.21 | 2350.54 | 2273.62 | 1414.67
G12 | 2425.79 | 2295.35 | 2185.64 | 2139.36 | 2088.64
G13 | 2434.16 | 2298.04 | 2190.04 | 2160.72 | 1528.93
G14 | 2447.71 | 2315.96 | 2205.43 | 1781.43 | 890.44
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Light Loads |  |  | 050 | University-Broad Street 115kV Line (SCL) (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3340.2267 | 3419.46 | 3428.97 | 3451.3 | 3262.25 | 3268.4 | 3294.42 | 2995.81 | 2996.94 | 3018.44 | 2565.89 | 2591.27 | 2594.75 | 2425.79 | 2434.16 | 2447.71
35F | 2662.3447 | 3308.51 | 3310.58 | 3324.61 | 3132.69 | 3144.92 | 3148.63 | 2848.63 | 2862.35 | 2874.28 | 2447.6 | 2456.51 | 2462.21 | 2295.35 | 2298.04 | 2315.96
45F | 2421.4047 | 3193.93 | 3206.48 | 3209.37 | 3035.14 | 3044.53 | 3052.41 | 2753.42 | 2763.72 | 2772.49 | 2326.7 | 2345.02 | 2350.54 | 2185.64 | 2190.04 | 2205.43
60F | 2941.0193 | 3151.28 | 3161.88 | 3159.25 | 2998.97 | 3011.37 | 3014.64 | 2719.2 | 2726.29 | 2742.34 | 2293.25 | 2308.49 | 2273.62 | 2139.36 | 2160.72 | 1781.43
70F | 3281.3993 | 3100.88 | 3099.89 | 2550.3 | 2941.21 | 2944.32 | 2314.67 | 2654.56 | 2637.76 | 1993.72 | 2231.47 | 2041.95 | 1414.67 | 2088.64 | 1528.93 | 890.44

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3438.12 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -491.4 | -491.64 | 3369.71 | 3419.46 | 1704.62 | FULL
G1 | 3448.01 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -491.59 | -491.81 | 3306.01 | 3428.97 | 1734.16 | FULL
G2 | 3470.41 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -491.33 | -491.58 | 3324.6 | 3451.3 | 1778 | FULL
G3 | 3279.13 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -501.05 | -502.2 | 3367.6 | 3262.25 | 1681.66 | FULL
G4 | 3285.61 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -502.38 | -503.27 | 3304.77 | 3268.4 | 1695.2 | FULL
G5 | 3311.59 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -501.94 | -502.54 | 3322.8 | 3294.42 | 1752.35 | FULL
G6 | 3009.77 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -508.53 | -508.33 | 3368.95 | 2995.81 | 1640.13 | FULL
G7 | 3011.19 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -509.37 | -508.22 | 3305.59 | 2996.94 | 1662.09 | FULL
G8 | 3032.87 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -507.64 | -506.73 | 3324.31 | 3018.44 | 1714.48 | FULL
G9 | 2576.62 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -516.94 | -516.29 | 3378.46 | 2565.89 | 1609.89 | FULL
G10 | 2600.72 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -518.96 | -518.2 | 3315.25 | 2591.27 | 1650.39 | FULL
G11 | 2604.8 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -517.09 | -517.81 | 3334.48 | 2594.75 | 1680.67 | FULL
G12 | 2433.99 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -516.21 | -516.39 | 3395.89 | 2425.79 | 1671.53 | FULL
G13 | 2442.19 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -515.9 | -516.98 | 3332.26 | 2434.16 | 1710.48 | FULL
G14 | 2457.05 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.68 | -516.87 | -517.05 | 3352.72 | 2447.71 | 1744.79 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3325.51 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -486.71 | -487.15 | 2690.43 | 3308.51 | 1694.88 | FULL
G1 | 3328.06 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -484.93 | -485.73 | 2627.09 | 3310.58 | 1723.14 | FULL
G2 | 3342.12 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -485.79 | -486.91 | 2646.3 | 3324.61 | 1753.97 | FULL
G3 | 3147.79 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -500.07 | -500.51 | 2688.52 | 3132.69 | 1652.88 | FULL
G4 | 3160.33 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -497.11 | -499.54 | 2625.18 | 3144.92 | 1696.44 | FULL
G5 | 3164.24 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -495.61 | -495.33 | 2644.24 | 3148.63 | 1726.5 | FULL
G6 | 2861.73 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -499.81 | -499.52 | 2689.83 | 2848.63 | 1612.22 | FULL
G7 | 2874.89 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -500.04 | -499.84 | 2626.54 | 2862.35 | 1655.33 | FULL
G8 | 2887.18 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -500.97 | -500.8 | 2646.21 | 2874.28 | 1682.85 | FULL
G9 | 2455.96 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -507.38 | -506.59 | 2700.85 | 2447.6 | 1594.78 | FULL
G10 | 2464.91 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -507.28 | -506.5 | 2638.05 | 2456.51 | 1628.22 | FULL
G11 | 2471.58 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -505.37 | -504.61 | 2658.32 | 2462.21 | 1650.38 | FULL
G12 | 2303.55 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -505.85 | -505.32 | 2719.05 | 2295.35 | 1657.19 | FULL
G13 | 2306.02 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -506.13 | -505.45 | 2656.68 | 2298.04 | 1676.28 | FULL
G14 | 2323.07 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -506.16 | -505.75 | 2677.88 | 2315.96 | 1713.44 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3209.8 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -483.57 | -482.89 | 2448.16 | 3193.93 | 1659.91 | FULL
G1 | 3222.37 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -483.52 | -482.95 | 2385.46 | 3206.48 | 1698.63 | FULL
G2 | 3225.43 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -479.12 | -478.67 | 2404.29 | 3209.37 | 1728.93 | FULL
G3 | 3049.72 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -490.98 | -490.55 | 2447.09 | 3035.14 | 1634.62 | FULL
G4 | 3059.05 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -490.47 | -490 | 2383.93 | 3044.53 | 1670.98 | FULL
G5 | 3066.92 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -489.82 | -489.35 | 2403.93 | 3052.41 | 1699.87 | FULL
G6 | 2764.76 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -494.19 | -493.7 | 2448.61 | 2753.42 | 1594.09 | FULL
G7 | 2775.38 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -494.38 | -494.02 | 2385.52 | 2763.72 | 1628.95 | FULL
G8 | 2784.01 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -490.26 | -489.8 | 2405.93 | 2772.49 | 1662.27 | FULL
G9 | 2334.44 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -494.91 | -494.15 | 2460.12 | 2326.7 | 1558.21 | FULL
G10 | 2353.3 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -495.15 | -494.34 | 2397.62 | 2345.02 | 1597.72 | FULL
G11 | 2359.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -492.11 | -491.55 | 2417.62 | 2350.54 | 1629.17 | FULL
G12 | 2191.78 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -493.97 | -493.14 | 2479.37 | 2185.64 | 1627.58 | FULL
G13 | 2196.49 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -492.09 | -491.27 | 2416.71 | 2190.04 | 1658.98 | FULL
G14 | 2211.75 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -493.72 | -492.95 | 2436.71 | 2205.43 | 1685.84 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3166.76 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -462.62 | -462.24 | 2970.76 | 3151.28 | 1602.07 | FULL
G1 | 3177.51 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -462.46 | -462.2 | 2906.96 | 3161.88 | 1638.26 | FULL
G2 | 3175.01 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -458.64 | -458.33 | 2925.08 | 3159.25 | 1665.12 | FULL
G3 | 3012.86 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -470.96 | -470.69 | 2969.38 | 2998.97 | 1580.1 | FULL
G4 | 3025.5 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -471.4 | -470.5 | 2905.72 | 3011.37 | 1615.67 | FULL
G5 | 3028.61 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -469.04 | -468.58 | 2924.5 | 3014.64 | 1632.68 | FULL
G6 | 2729.91 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -471.17 | -470.69 | 2971.1 | 2719.2 | 1542.44 | FULL
G7 | 2737.61 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -470.29 | -469.86 | 2907.42 | 2726.29 | 1575.1 | FULL
G8 | 2753.34 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -471.88 | -471.5 | 2926.24 | 2742.34 | 1602.79 | FULL
G9 | 2301.63 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -472.83 | -472.21 | 2981.57 | 2293.25 | 1507.48 | FULL
G10 | 2316.08 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -474.76 | -474.19 | 2917.94 | 2308.49 | 1544.16 | FULL
G11 | 2280.85 | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -3.33 | -199.56 | -199.56 | 2934.43 | 2273.62 | 1538.17 | FULL
G12 | 2145.04 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -473.37 | -472.57 | 2999.7 | 2139.36 | 1550.57 | FULL
G13 | 2167.38 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -474.38 | -473.6 | 2936.27 | 2160.72 | 1599.42 | FULL
G14 | 1785.62 | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -3.33 | -197.15 | -197.18 | 2938.22 | 1781.43 | 1434.83 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3115.62 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -451.75 | -451.31 | 3322.58 | 3100.88 | 1570.85 | FULL
G1 | 3114.42 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -450.09 | -449.68 | 3256.79 | 3099.89 | 1594.56 | FULL
G2 | 2559.51 | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -3.33 | -178.62 | -178.61 | 3253.73 | 2550.3 | 1332.58 | FULL
G3 | 2953.52 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -457.92 | -457.11 | 3321.3 | 2941.21 | 1545.13 | FULL
G4 | 2957.16 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -456.79 | -455.66 | 3254.68 | 2944.32 | 1578.21 | FULL
G5 | 2322.28 | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -3.33 | -178.07 | -178.13 | 3250.95 | 2314.67 | 1260.36 | FULL
G6 | 2665.25 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -457.21 | -456.24 | 3322.85 | 2654.56 | 1502.99 | FULL
G7 | 2647.73 | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -3.33 | -178.78 | -178.84 | 3255.84 | 2637.76 | 1523.22 | FULL
G8 | 1999.05 | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -3.33 | -178.06 | -178.11 | 3251.75 | 1993.72 | 1199.59 | FULL
G9 | 2238.93 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -459.66 | -458.77 | 3333.45 | 2231.47 | 1468.41 | FULL
G10 | 2048.02 | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -3.33 | -177.73 | -177.72 | 3260.74 | 2041.95 | 1390.78 | FULL
G11 | 1416.69 | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -3.33 | -178.11 | -178.14 | 3258.25 | 1414.67 | 1080.26 | FULL
G12 | 2095.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -459.59 | -458.58 | 3350.58 | 2088.64 | 1527.17 | FULL
G13 | 1532.2 | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -3.33 | -178.54 | -178.62 | 3264.24 | 1528.93 | 1264.75 | FULL
G14 | 889.87 | Branch BROAD ST (46409) TO CANAL (46411) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -3.33 | -177.5 | -177.48 | 3263.26 | 890.44 | 941 | FULL
050WINTER09v1NSL