## 25F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 022
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3331.9713
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2458.48 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3233.16 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2801.42 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3531.35 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 3233.16 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3641.53 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 140 | 2599.83 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3042.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2986.04 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 948.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3531.35 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2801.42 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2890.65 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2986.04 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3248.93 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3248.93 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3641.53 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3134.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 3239.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 1049.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3134.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2458.48 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3042.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2599.83 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1165.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2890.65 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1049.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3239.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 948.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1165.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 022
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2655.4393
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3283.17 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3216.66 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3364.06 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3500.97 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 3216.66 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3590.72 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 140 | 3448.08 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2281.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3471 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 235.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3500.97 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 3364.06 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 3569.9 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 3471 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3579.02 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3579.02 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
525 | 775 | 3590.72 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 2384.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2494.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 321.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2384.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3283.17 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2281.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 3448.08 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 425.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3569.9 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1400 | 460 | 321.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2494.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 235.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 425.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 022
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2409.204
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3278.69 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 3231.41 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3313.07 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 3157.52 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 3231.41 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3468.05 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 140 | 3121.44 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 1355.98 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3126.19 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -999.6 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3157.52 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 3313.07 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3296.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 3126.19 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3469.4 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3469.4 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
525 | 775 | 3468.05 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 1458.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1570.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -917.71 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1458.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3278.69 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1355.98 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 3121.44 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -860.89 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3296.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -917.71 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1570.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -999.6 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -860.89 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 022
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2924.0347
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2252.99 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2808.45 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2749.28 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2915.48 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2808.45 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 3116.62 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2369.16 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1774.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2920.02 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -464.62 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2915.48 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2749.28 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2687.71 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2920.02 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3086.22 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3086.22 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3116.62 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 1869.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1989.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -405.27 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1869.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2252.99 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1774.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2369.16 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | -298.69 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2687.71 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | -405.27 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1989.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -464.62 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -298.69 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 022
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3268.412
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1687.56 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2459.35 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2072.99 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2594.72 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2459.35 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2826.92 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1888.99 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1884.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2255.31 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -317.69 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2594.72 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2072.99 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2185.79 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2255.31 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2519.92 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2519.92 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2826.92 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1989.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2086.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -271.53 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1989.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1687.56 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1884.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1888.99 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | -198.61 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2185.79 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | -271.53 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2086.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -317.69 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -198.61 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
G0 | 2458.48 | 3283.17 | 3278.69 | 2252.99 | 1687.56
G1 | 2801.42 | 3364.06 | 3313.07 | 2749.28 | 2072.99 | Season/Year: | WINTER 2009
G2 | 3233.16 | 3216.66 | 3231.41 | 2808.45 | 2459.35 | Direction: | South-to-North (SN)
G3 | 2599.83 | 3448.08 | 3121.44 | 2369.16 | 1888.99 | Case Loads: | Light Loads
G4 | 2986.04 | 3471 | 3126.19 | 2920.02 | 2255.31 | Outage: | 022
G5 | 3531.35 | 3500.97 | 3157.52 | 2915.48 | 2594.72 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2890.65 | 3569.9 | 3296.32 | 2687.71 | 2185.79 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3248.93 | 3579.02 | 3469.4 | 3086.22 | 2519.92 | Study Person: | JGO7470
G8 | 3641.53 | 3590.72 | 3468.05 | 3116.62 | 2826.92 | Source: | 022WINTER09v1SNL
G9 | 3239.36 | 2494.73 | 1570.94 | 1989.1 | 2086.14
G10 | 3134.21 | 2384.83 | 1458.51 | 1869.85 | 1989.58
G11 | 3042.05 | 2281.94 | 1355.98 | 1774.19 | 1884.2
G12 | 1165.91 | 425.71 | -860.89 | -298.69 | -198.61
G13 | 1049.5 | 321.82 | -917.71 | -405.27 | -271.53
G14 | 948.81 | 235.61 | -999.6 | -464.62 | -317.69
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Light Loads |  |  | 022 | Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3331.9713 | 2458.48 | 2801.42 | 3233.16 | 2599.83 | 2986.04 | 3531.35 | 2890.65 | 3248.93 | 3641.53 | 3239.36 | 3134.21 | 3042.05 | 1165.91 | 1049.5 | 948.81
35F | 2655.4393 | 3283.17 | 3364.06 | 3216.66 | 3448.08 | 3471 | 3500.97 | 3569.9 | 3579.02 | 3590.72 | 2494.73 | 2384.83 | 2281.94 | 425.71 | 321.82 | 235.61
45F | 2409.204 | 3278.69 | 3313.07 | 3231.41 | 3121.44 | 3126.19 | 3157.52 | 3296.32 | 3469.4 | 3468.05 | 1570.94 | 1458.51 | 1355.98 | -860.89 | -917.71 | -999.6
60F | 2924.0347 | 2252.99 | 2749.28 | 2808.45 | 2369.16 | 2920.02 | 2915.48 | 2687.71 | 3086.22 | 3116.62 | 1989.1 | 1869.85 | 1774.19 | -298.69 | -405.27 | -464.62
70F | 3268.412 | 1687.56 | 2072.99 | 2459.35 | 1888.99 | 2255.31 | 2594.72 | 2185.79 | 2519.92 | 2826.92 | 2086.14 | 1989.58 | 1884.2 | -198.61 | -271.53 | -317.69

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2460.19 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 13.43 | 744.6 | 744.62 | 3369.23 | 2458.48 | -1657.21 | FULL
G1 | 2800.61 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 13.43 | 740.37 | 740.74 | 3317.02 | 2801.42 | -1828.45 | FULL
G2 | 3234.01 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.35 | 531.35 | 531.53 | 3347.32 | 3233.16 | -2035.32 | FULL
G3 | 2600.74 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 13.43 | 740.21 | 740.41 | 3370.74 | 2599.83 | -1671.35 | FULL
G4 | 2986.2 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 13.43 | 742.63 | 742.3 | 3319.97 | 2986.04 | -1868.93 | FULL
G5 | 3530.43 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65 | -2690.81 | -2689.76 | 3358.72 | 3531.35 | -2148.84 | CTG_FAIL_IN_FULL
G6 | 2890.59 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 13.43 | 745 | 745.21 | 3374.14 | 2890.65 | -1728.07 | FULL
G7 | 3248.28 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 13.43 | 741.99 | 742.34 | 3324.31 | 3248.93 | -1905.94 | FULL
G8 | 3641.22 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3602.34 | 3604.01 | 3353.39 | 3641.53 | -2095.85 | FULL
G9 | 3238.93 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -475.19 | -475.14 | 3375.7 | 3239.36 | -1717.35 | FULL
G10 | 3134.48 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -472.43 | -472.35 | 3300.7 | 3134.21 | -1626.88 | FULL
G11 | 3042.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -471.14 | -471.09 | 3310.47 | 3042.05 | -1545.11 | FULL
G12 | 1166.48 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -452.72 | -452.65 | 3325.64 | 1165.91 | -389.1 | FULL
G13 | 1049.88 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -452.14 | -452.1 | 3258.28 | 1049.5 | -292.14 | FULL
G14 | 950.02 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -452.29 | -452.26 | 3273.94 | 948.81 | -204.79 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3285.02 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13 | 748.69 | 748.61 | 2722 | 3283.17 | -2067.27 | CTG_FAIL_IN_FULL
G1 | 3365.1 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.35 | 517.55 | 517.71 | 2656.93 | 3364.06 | -2086.29 | FULL
G2 | 3216.32 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.35 | 511.17 | 511.28 | 2660.18 | 3216.66 | -1972.78 | FULL
G3 | 3449.39 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13 | 746.97 | 747.23 | 2724.55 | 3448.08 | -2102.89 | CTG_FAIL_IN_FULL
G4 | 3472 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65 | -2612.87 | -2613.14 | 2657.21 | 3471 | -2082.51 | CTG_FAIL_IN_FULL
G5 | 3499.27 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65 | -2621.51 | -2621.93 | 2669.87 | 3500.97 | -2073.73 | CTG_FAIL_IN_FULL
G6 | 3570.1 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3532.55 | 3535.21 | 2721.7 | 3569.9 | -2055.42 | FULL
G7 | 3578.4 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3540.38 | 3541.3 | 2652.69 | 3579.02 | -2029.64 | FULL
G8 | 3590.9 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3553.28 | 3551.82 | 2665.5 | 3590.72 | -2005.91 | FULL
G9 | 2496.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -454.39 | -454.3 | 2664.53 | 2494.73 | -1228.88 | FULL
G10 | 2386.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -454.92 | -454.82 | 2594.45 | 2384.83 | -1136.71 | FULL
G11 | 2282.22 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -453.91 | -453.8 | 2606.43 | 2281.94 | -1048.42 | FULL
G12 | 425.11 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -443.78 | -444.03 | 2648.98 | 425.71 | 86.47 | FULL
G13 | 322.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -444.54 | -444.7 | 2584.35 | 321.82 | 175.86 | FULL
G14 | 235.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -445.84 | -445.76 | 2602.22 | 235.61 | 254.27 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3279.16 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65 | -2534.17 | -2534.37 | 2477.54 | 3278.69 | -2029.39 | CTG_FAIL_IN_FULL
G1 | 3313.18 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65 | -2542.21 | -2542.15 | 2408.09 | 3313.07 | -2019.56 | CTG_FAIL_IN_FULL
G2 | 3232.66 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.35 | 495.25 | 494.97 | 2416.12 | 3231.41 | -1943.71 | FULL
G3 | 3120.35 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.41 | -2400.13 | -2398.87 | 2469.69 | 3121.44 | -1870.48 | FULL
G4 | 3127.33 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.41 | -2327.61 | -2326.49 | 2400.06 | 3126.19 | -1851.83 | FULL
G5 | 3156.19 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.41 | -2332.19 | -2333.73 | 2414.44 | 3157.52 | -1839.51 | FULL
G6 | 3295.85 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.41 | -2328.41 | -2326.6 | 2468.37 | 3296.32 | -1860.87 | FULL
G7 | 3469.9 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3433.63 | 3435.08 | 2403.07 | 3469.4 | -1921.34 | FULL
G8 | 3466.73 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3430.57 | 3431.49 | 2415.76 | 3468.05 | -1893.49 | FULL
G9 | 1571.69 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -412.63 | -412.56 | 2405.54 | 1570.94 | -668.55 | FULL
G10 | 1459.05 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -411.61 | -411.55 | 2337.19 | 1458.51 | -573.89 | FULL
G11 | 1355.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -411.32 | -411.27 | 2351.95 | 1355.98 | -485.69 | FULL
G12 | -862.22 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.04 | -421.76 | -421.67 | 2425.08 | -860.89 | 828.17 | FULL
G13 | -919.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.04 | -423.45 | -423.41 | 2362.68 | -917.71 | 890.96 | FULL
G14 | -1000.78 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.04 | -424.24 | -424.19 | 2382.48 | -999.6 | 967.13 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2254.39 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.88 | 667.72 | 668.01 | 2964.32 | 2252.99 | -1488.51 | FULL
G1 | 2750.16 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 13.43 | 676.01 | 676.31 | 2915.22 | 2749.28 | -1738.09 | FULL
G2 | 2808.6 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.41 | -2201.6 | -2200.03 | 2933.32 | 2808.45 | -1742.46 | FULL
G3 | 2370.03 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.88 | 663.34 | 663.54 | 2966.33 | 2369.16 | -1488.21 | FULL
G4 | 2918.64 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 13.43 | 675.84 | 676.11 | 2917.97 | 2920.02 | -1770.76 | FULL
G5 | 2915.69 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.41 | -2212.16 | -2213.81 | 2932.3 | 2915.48 | -1741.41 | FULL
G6 | 2687.88 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.88 | 671.2 | 673.94 | 2971.08 | 2687.71 | -1553.92 | FULL
G7 | 3086.71 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.41 | -2272.79 | -2273.96 | 2919.93 | 3086.22 | -1747.96 | FULL
G8 | 3116.96 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.41 | -2225.19 | -2226.33 | 2932.65 | 3116.62 | -1742.06 | FULL
G9 | 1988.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -417.17 | -417.09 | 2941.11 | 1989.1 | -950.75 | FULL
G10 | 1869.74 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -415.18 | -415.1 | 2870.8 | 1869.85 | -852.2 | FULL
G11 | 1775.71 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -416.03 | -415.96 | 2883.28 | 1774.19 | -771.77 | FULL
G12 | -298.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.04 | -416.46 | -416.42 | 2941.58 | -298.69 | 473.29 | FULL
G13 | -404.94 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.04 | -416.72 | -416.66 | 2876.72 | -405.27 | 562.35 | FULL
G14 | -464.67 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.04 | -418.22 | -418.12 | 2893.91 | -464.62 | 627.6 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1687.4 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.88 | 647.28 | 647.15 | 3301.09 | 1687.56 | -1178.12 | FULL
G1 | 2074.57 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.88 | 643.94 | 644.3 | 3244.43 | 2072.99 | -1368.94 | FULL
G2 | 2459.38 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.88 | 643.57 | 642.53 | 3272.44 | 2459.35 | -1555.47 | FULL
G3 | 1889.81 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.88 | 651.87 | 652.24 | 3303.27 | 1888.99 | -1228.34 | FULL
G4 | 2256.67 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.88 | 645.19 | 645.37 | 3248.18 | 2255.31 | -1399.07 | FULL
G5 | 2594.91 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.88 | 637.91 | 638.17 | 3274.63 | 2594.72 | -1569.64 | FULL
G6 | 2186.03 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.88 | 654.4 | 654.39 | 3307.22 | 2185.79 | -1282.66 | FULL
G7 | 2520.17 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.88 | 641.99 | 641.58 | 3250.91 | 2519.92 | -1437.1 | FULL
G8 | 2827.84 | Branch BERYDALE (42507) TO TALBOT S (42501) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.88 | 632.56 | 632.61 | 3278.14 | 2826.92 | -1583.17 | FULL
G9 | 2087.28 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -418.62 | -418.54 | 3299.94 | 2086.14 | -1019.7 | FULL
G10 | 1989.33 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -419.43 | -419.37 | 3229.28 | 1989.58 | -936.65 | FULL
G11 | 1886.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.6 | -418.69 | -418.69 | 3241.9 | 1884.2 | -846.63 | FULL
G12 | -198.19 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.04 | -415.35 | -415.33 | 3296.33 | -198.61 | 408.13 | FULL
G13 | -271.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.04 | -416.65 | -416.6 | 3230.77 | -271.53 | 479.17 | FULL
G14 | -317.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.04 | -418.57 | -418.51 | 3247.65 | -317.69 | 534.24 | FULL
022WINTER09v1SNL