## 25F nomo
Custer 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 018
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3335.75
Gen Level |  | Trans | Worst | Limiting |  |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [6 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3073.97 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  |  | G3 | 100 | 775 | 3091.62 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
100 | 460 | 3087.24 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  |  | G6 | 260 | 775 | 3110.54 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
100 | 775 | 3091.62 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  |  | G9 | 525 | 775 | 3036.16 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3095.25 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  |  | G12 | 1000 | 775 | 2610.62 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3093.51 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  |  | G15 | 1400 | 775 | 2473.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3110.54 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  |  | G2 | 100 | 465 | 3087.24 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
525 | 140 | 3013.94 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G5 | 260 | 460 | 3093.51 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
525 | 460 | 3016.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G8 | 525 | 460 | 3016.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3036.16 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G11 | 1000 | 460 | 2597.15 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2584.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G14 | 1400 | 460 | 2462.22 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2597.15 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G1 | 100 | 140 | 3073.97 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
1000 | 775 | 2610.62 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G4 | 260 | 140 | 3095.25 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
1400 | 140 | 2447.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G7 | 525 | 140 | 3013.94 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2462.22 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G10 | 1000 | 140 | 2584.6 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2473.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G13 | 1400 | 140 | 2447.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450
G1
789

## 35F nomo
Custer 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 018
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2660.2993
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3101.21 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3110.48 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
100 | 460 | 3108.07 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3134 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
100 | 775 | 3110.48 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2899.51 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3126.47 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2478.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3127.67 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2339.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3134 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3108.07 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
525 | 140 | 2889.9 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3127.67 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
525 | 460 | 2898.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2898.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2899.51 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2473.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2468.15 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2326.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2473.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3101.21 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
1000 | 775 | 2478.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 3126.47 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
1400 | 140 | 2316.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2889.9 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2326.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2468.15 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2339.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2316.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Custer 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 018
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2420.6987
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3117.27 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3124.69 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
100 | 460 | 3123.22 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3083.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3124.69 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2799.57 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3065.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2373.78 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3071.94 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2225.48 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3083.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3123.22 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
525 | 140 | 2780.05 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3071.94 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2789.15 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2789.15 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2799.57 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2367.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2360.58 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2212.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2367.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3117.27 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
1000 | 775 | 2373.78 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 3065.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2190.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2780.05 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2212.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2360.58 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2225.48 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2190.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Custer 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 018
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2941.8147
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3099.83 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3109.72 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
100 | 460 | 3106.54 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3039.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3109.72 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2760.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3027.61 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2327.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3035.09 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2189.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3039.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 3106.54 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
525 | 140 | 2747.79 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3035.09 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2746.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2746.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2760.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2324.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2312.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2176.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2324.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3099.83 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
1000 | 775 | 2327.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 3027.61 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2167.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2747.79 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2176.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2312.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2189.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2167.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Custer 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 018
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3293.9953
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3087.23 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3102.63 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
100 | 460 | 3091.29 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2985.22 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3102.63 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2708.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2952.88 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2272.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2959.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2127.98 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2985.22 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3091.29 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
525 | 140 | 2681 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2959.46 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2691.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2691.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2708.97 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2264.16 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2255.31 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2118.55 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2264.16 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3087.23 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV]
1000 | 775 | 2272.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2952.88 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2105.82 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2681 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2118.55 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2255.31 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2127.98 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2105.82 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Custer 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
G0 | 3073.97 | 3101.21 | 3117.27 | 3099.83 | 3087.23
G1 | 3087.24 | 3108.07 | 3123.22 | 3106.54 | 3091.29 | Season/Year: | WINTER 2009
G2 | 3091.62 | 3110.48 | 3124.69 | 3109.72 | 3102.63 | Direction: | North-to-South (NS)
G3 | 3095.25 | 3126.47 | 3065.02 | 3027.61 | 2952.88 | Case Loads: | Light Loads
G4 | 3093.51 | 3127.67 | 3071.94 | 3035.09 | 2959.46 | Outage: | 018
G5 | 3110.54 | 3134 | 3083.26 | 3039.92 | 2985.22 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3013.94 | 2889.9 | 2780.05 | 2747.79 | 2681 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3016.5 | 2898.06 | 2789.15 | 2746.5 | 2691.25 | Study Person: | FRP9899
G8 | 3036.16 | 2899.51 | 2799.57 | 2760.46 | 2708.97 | Source: | 018WINTER09v1NSL
G9 | 2584.6 | 2468.15 | 2360.58 | 2312.49 | 2255.31
G10 | 2597.15 | 2473.68 | 2367.06 | 2324.47 | 2264.16
G11 | 2610.62 | 2478.06 | 2373.78 | 2327.29 | 2272.43
G12 | 2447.02 | 2316.56 | 2190.28 | 2167.47 | 2105.82
G13 | 2462.22 | 2326.56 | 2212.26 | 2176.77 | 2118.55
G14 | 2473.68 | 2339.01 | 2225.48 | 2189.75 | 2127.98
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Light Loads |  |  | 018 | Custer 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3335.75 | 3073.97 | 3087.24 | 3091.62 | 3095.25 | 3093.51 | 3110.54 | 3013.94 | 3016.5 | 3036.16 | 2584.6 | 2597.15 | 2610.62 | 2447.02 | 2462.22 | 2473.68
35F | 2660.2993 | 3101.21 | 3108.07 | 3110.48 | 3126.47 | 3127.67 | 3134 | 2889.9 | 2898.06 | 2899.51 | 2468.15 | 2473.68 | 2478.06 | 2316.56 | 2326.56 | 2339.01
45F | 2420.6987 | 3117.27 | 3123.22 | 3124.69 | 3065.02 | 3071.94 | 3083.26 | 2780.05 | 2789.15 | 2799.57 | 2360.58 | 2367.06 | 2373.78 | 2190.28 | 2212.26 | 2225.48
60F | 2941.8147 | 3099.83 | 3106.54 | 3109.72 | 3027.61 | 3035.09 | 3039.92 | 2747.79 | 2746.5 | 2760.46 | 2312.49 | 2324.47 | 2327.29 | 2167.47 | 2176.77 | 2189.75
70F | 3293.9953 | 3087.23 | 3091.29 | 3102.63 | 2952.88 | 2959.46 | 2985.22 | 2681 | 2691.25 | 2708.97 | 2255.31 | 2264.16 | 2272.43 | 2105.82 | 2118.55 | 2127.98

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3088.7 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1812.95 | 1810.46 | 3355.24 | 3073.97 | 1546.18 | FULL
G1 | 3102.33 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1814.85 | 1812.32 | 3290.7 | 3087.24 | 1583.33 | FULL
G2 | 3106.73 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1811.61 | 1809.37 | 3308.95 | 3091.62 | 1619.55 | FULL
G3 | 3110.8 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1807.46 | 1806.81 | 3361.32 | 3095.25 | 1614.45 | FULL
G4 | 3108.74 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1801.99 | 1801.45 | 3296.69 | 3093.51 | 1641.97 | FULL
G5 | 3125.95 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1806.56 | 1805.9 | 3314.41 | 3110.54 | 1682.49 | FULL
G6 | 3028.34 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -500.45 | -500.26 | 3369.05 | 3013.94 | 1684.61 | FULL
G7 | 3031.14 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -499.68 | -499.7 | 3305.63 | 3016.5 | 1696.76 | FULL
G8 | 3050.75 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -498.65 | -498.36 | 3324.63 | 3036.16 | 1746.59 | FULL
G9 | 2594.74 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -511.81 | -512.38 | 3378.67 | 2584.6 | 1623.78 | FULL
G10 | 2607.37 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -512.87 | -512.28 | 3315.97 | 2597.15 | 1658 | FULL
G11 | 2620.87 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -511.61 | -511.19 | 3333.91 | 2610.62 | 1699.52 | FULL
G12 | 2456.14 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -513.46 | -513.65 | 3396.36 | 2447.02 | 1684.78 | FULL
G13 | 2471.09 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -514.05 | -514.27 | 3332.3 | 2462.22 | 1731.15 | FULL
G14 | 2483.04 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -513.25 | -513.51 | 3352.42 | 2473.68 | 1765.28 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3116.46 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1811.69 | 1810.72 | 2681.05 | 3101.21 | 1615.27 | FULL
G1 | 3123.68 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1812.81 | 1812.2 | 2618.17 | 3108.07 | 1644.54 | FULL
G2 | 3125.99 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1810.62 | 1809.99 | 2636.6 | 3110.48 | 1668.31 | FULL
G3 | 3141.97 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1810.53 | 1809.56 | 2687.73 | 3126.47 | 1685.45 | FULL
G4 | 3143.4 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1805.44 | 1804.55 | 2625.12 | 3127.67 | 1712.68 | FULL
G5 | 3149.61 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1805.83 | 1804.94 | 2643.33 | 3134 | 1740.55 | FULL
G6 | 2902.07 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -496.06 | -496.41 | 2689.79 | 2889.9 | 1663.39 | FULL
G7 | 2911.15 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -496.09 | -497.76 | 2626.05 | 2898.06 | 1697.46 | FULL
G8 | 2912.75 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.92 | -495.12 | -494.9 | 2646.26 | 2899.51 | 1720.11 | FULL
G9 | 2477.07 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -503.68 | -502.8 | 2700.87 | 2468.15 | 1616.66 | FULL
G10 | 2482.89 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -502.35 | -501.45 | 2638.02 | 2473.68 | 1647 | FULL
G11 | 2487.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -499.81 | -498.95 | 2658.26 | 2478.06 | 1664.03 | FULL
G12 | 2324.3 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -502.35 | -501.74 | 2718.87 | 2316.56 | 1673.06 | FULL
G13 | 2333.59 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -502.94 | -502.16 | 2657.39 | 2326.56 | 1690.45 | FULL
G14 | 2346.39 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -501.99 | -500.95 | 2676.98 | 2339.01 | 1730.39 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3132.61 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1812.96 | 1810.81 | 2444.58 | 3117.27 | 1650.91 | FULL
G1 | 3138.8 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1812.05 | 1811.14 | 2381.72 | 3123.22 | 1682.1 | FULL
G2 | 3140.42 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1808.26 | 1807.46 | 2400.53 | 3124.69 | 1710.25 | FULL
G3 | 3079.35 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -483.72 | -483.21 | 2447.59 | 3065.02 | 1679.71 | FULL
G4 | 3086.12 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -482.36 | -481.88 | 2383.73 | 3071.94 | 1713.23 | FULL
G5 | 3097.64 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -482 | -481.59 | 2403.69 | 3083.26 | 1745.38 | FULL
G6 | 2792.4 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -487.05 | -486.5 | 2448.76 | 2780.05 | 1631.17 | FULL
G7 | 2801.37 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -487.14 | -486.59 | 2385.58 | 2789.15 | 1663.06 | FULL
G8 | 2811.84 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -486.36 | -485.94 | 2405.9 | 2799.57 | 1693.77 | FULL
G9 | 2368.57 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -494.11 | -493.16 | 2459.48 | 2360.58 | 1587.52 | FULL
G10 | 2374.17 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -492.38 | -491.47 | 2397.59 | 2367.06 | 1617.52 | FULL
G11 | 2382.08 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -491.11 | -490.18 | 2417.26 | 2373.78 | 1648.04 | FULL
G12 | 2196.95 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -488.25 | -487.58 | 2479.04 | 2190.28 | 1631.59 | FULL
G13 | 2219.14 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -490.65 | -489.73 | 2417.28 | 2212.26 | 1670.58 | FULL
G14 | 2232.04 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -490.99 | -490.36 | 2437.75 | 2225.48 | 1691.06 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3114.73 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1809.61 | 1809.03 | 2968.76 | 3099.83 | 1607.75 | FULL
G1 | 3122.02 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1811.63 | 1810.95 | 2904.74 | 3106.54 | 1638.51 | FULL
G2 | 3125.3 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1811.23 | 1810.57 | 2922.95 | 3109.72 | 1662.15 | FULL
G3 | 3042.44 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -463.8 | -462.86 | 2969.42 | 3027.61 | 1625.13 | FULL
G4 | 3050.02 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -463.07 | -462.66 | 2905.62 | 3035.09 | 1656.55 | FULL
G5 | 3054.07 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -462.05 | -461.85 | 2924.03 | 3039.92 | 1681.55 | FULL
G6 | 2759.06 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -467.92 | -467.4 | 2970.98 | 2747.79 | 1579.74 | FULL
G7 | 2758.63 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -466.67 | -466.19 | 2907.34 | 2746.5 | 1605.25 | FULL
G8 | 2772.19 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -466.54 | -466.17 | 2925.65 | 2760.46 | 1640.2 | FULL
G9 | 2320.21 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -468.93 | -468.15 | 2981.68 | 2312.49 | 1528.62 | FULL
G10 | 2332.92 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -472.68 | -471.89 | 2917.57 | 2324.47 | 1561.5 | FULL
G11 | 2334.41 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -468.04 | -467.12 | 2936.85 | 2327.29 | 1585.96 | FULL
G12 | 2174.09 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -470.28 | -469.33 | 2999.37 | 2167.47 | 1587.2 | FULL
G13 | 2182.94 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -470.58 | -469.62 | 2936.5 | 2176.77 | 1609.56 | FULL
G14 | 2196.83 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -469.76 | -468.76 | 2955.76 | 2189.75 | 1650.17 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3101.98 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1807.05 | 1806.49 | 3322.92 | 3087.23 | 1590.54 | FULL
G1 | 3106.38 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1807.37 | 1807.01 | 3258.95 | 3091.29 | 1609.34 | FULL
G2 | 3117.58 | Branch CUST BNK2 (95011) TO CUST BNK2 (95006) CKT 2 [500.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 1808.44 | 1807.83 | 3276.37 | 3102.63 | 1655.15 | FULL
G3 | 2966.35 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -448.04 | -447.78 | 3321.68 | 2952.88 | 1579.72 | FULL
G4 | 2973.37 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -447.75 | -447.47 | 3257.53 | 2959.46 | 1606.15 | FULL
G5 | 2999.39 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -448.47 | -448.16 | 3275.53 | 2985.22 | 1649.16 | FULL
G6 | 2692.06 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -453.57 | -452.47 | 3322.8 | 2681 | 1539.25 | FULL
G7 | 2702.17 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -452.46 | -452.23 | 3259.33 | 2691.25 | 1561.83 | FULL
G8 | 2719.96 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -453.38 | -452.27 | 3277.16 | 2708.97 | 1600.92 | FULL
G9 | 2261.81 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -455.64 | -454.92 | 3334.36 | 2255.31 | 1482.86 | FULL
G10 | 2271.73 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -455.88 | -455.13 | 3269.71 | 2264.16 | 1521.25 | FULL
G11 | 2280.04 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -455.55 | -454.81 | 3287.94 | 2272.43 | 1557.41 | FULL
G12 | 2112.02 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -456.26 | -455.13 | 3351.39 | 2105.82 | 1544.96 | FULL
G13 | 2125.05 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -456.07 | -455.11 | 3287.47 | 2118.55 | 1586.12 | FULL
G14 | 2133.99 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -454.94 | -454.21 | 3306.79 | 2127.98 | 1605.88 | FULL
018WINTER09v1NSL