## 25F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 001R2
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3169.8847
Gen Level |  | Trans | Worst | Limiting |  |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [6 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2682.34 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  |  | G3 | 100 | 775 | 2690.54 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2687.5 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  |  | G6 | 260 | 775 | 2787.38 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2690.54 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  |  | G9 | 525 | 775 | 3041.5 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2773.68 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  |  | G12 | 1000 | 775 | 2511.48 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2786.23 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  |  | G15 | 1400 | 775 | 2507.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2787.38 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  |  | G2 | 100 | 465 | 2687.5 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3027.17 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  |  | G5 | 260 | 460 | 2786.23 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3042.52 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  |  | G8 | 525 | 460 | 3042.52 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
525 | 775 | 3041.5 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  |  | G11 | 1000 | 460 | 2510.57 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2504.49 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  |  | G14 | 1400 | 460 | 2496.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2510.57 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  |  | G1 | 100 | 140 | 2682.34 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2511.48 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  |  | G4 | 260 | 140 | 2773.68 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2486.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G7 | 525 | 140 | 3027.17 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 460 | 2496.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G10 | 1000 | 140 | 2504.49 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 2507.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G13 | 1400 | 140 | 2486.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450
G1
789

## 35F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 001R2
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2508.7887
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2725.16 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2738.59 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2729.99 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2824.63 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2738.59 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2976.16 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2816.88 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2544.55 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2828.06 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2393.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2824.63 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2729.99 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2961.68 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2828.06 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2970.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2970.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2976.16 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2500.4 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2496.13 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 2377.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2500.4 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2725.16 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2544.55 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2816.88 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2348.54 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2961.68 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2377.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2496.13 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 2393.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2348.54 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 001R2
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2275.8593
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2657.59 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2672.09 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2662.33 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2766.33 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2672.09 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2870.39 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2751.43 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2420.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2750.61 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2262.07 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2766.33 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2662.33 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2844.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2750.61 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2863.56 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2863.56 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2870.39 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2401.47 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2402.62 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2256.69 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2401.47 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2657.59 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2420.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2751.43 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2253.13 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2844.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2256.69 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2402.62 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2262.07 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2253.13 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 001R2
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2800.5707
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2615.2 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2613.43 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2610.6 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2718.82 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2613.43 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2847.01 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2711.99 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2389.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2714.27 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2237.34 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2718.82 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 2610.6 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2819.77 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2714.27 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2827.26 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2827.26 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2847.01 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2382.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2374.82 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2227.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2382.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2615.2 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2389.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2711.99 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2216.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2819.77 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2227.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2374.82 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2237.34 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2216.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 001R2
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3153.3507
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2600.79 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2614.08 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2606.46 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2709.76 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2614.08 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2773.73 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2690.37 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2330.77 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2703.93 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2163.65 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2709.76 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2606.46 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2760.99 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2703.93 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2770.28 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2770.28 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2773.73 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2314.11 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2300.38 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2168.23 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2314.11 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2600.79 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2330.77 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2690.37 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2160.92 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2760.99 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2168.23 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2300.38 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2163.65 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2160.92 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
G0 | 2682.34 | 2725.16 | 2657.59 | 2615.2 | 2600.79
G1 | 2687.5 | 2729.99 | 2662.33 | 2610.6 | 2606.46 | Season/Year: | WINTER 2009
G2 | 2690.54 | 2738.59 | 2672.09 | 2613.43 | 2614.08 | Direction: | North-to-South (NS)
G3 | 2773.68 | 2816.88 | 2751.43 | 2711.99 | 2690.37 | Case Loads: | Light Loads
G4 | 2786.23 | 2828.06 | 2750.61 | 2714.27 | 2703.93 | Outage: | 001R2
G5 | 2787.38 | 2824.63 | 2766.33 | 2718.82 | 2709.76 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3027.17 | 2961.68 | 2844.01 | 2819.77 | 2760.99 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3042.52 | 2970.49 | 2863.56 | 2827.26 | 2770.28 | Study Person: | FRP9899
G8 | 3041.5 | 2976.16 | 2870.39 | 2847.01 | 2773.73 | Source: | 001R2WINTER09v5NSL
G9 | 2504.49 | 2496.13 | 2402.62 | 2374.82 | 2300.38
G10 | 2510.57 | 2500.4 | 2401.47 | 2382.42 | 2314.11
G11 | 2511.48 | 2544.55 | 2420.26 | 2389.63 | 2330.77
G12 | 2486.96 | 2348.54 | 2253.13 | 2216.29 | 2160.92
G13 | 2496.06 | 2377.26 | 2256.69 | 2227.42 | 2168.23
G14 | 2507.77 | 2393.92 | 2262.07 | 2237.34 | 2163.65
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Light Loads |  |  | 001R2 | Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3169.8847 | 2682.34 | 2687.5 | 2690.54 | 2773.68 | 2786.23 | 2787.38 | 3027.17 | 3042.52 | 3041.5 | 2504.49 | 2510.57 | 2511.48 | 2486.96 | 2496.06 | 2507.77
35F | 2508.7887 | 2725.16 | 2729.99 | 2738.59 | 2816.88 | 2828.06 | 2824.63 | 2961.68 | 2970.49 | 2976.16 | 2496.13 | 2500.4 | 2544.55 | 2348.54 | 2377.26 | 2393.92
45F | 2275.8593 | 2657.59 | 2662.33 | 2672.09 | 2751.43 | 2750.61 | 2766.33 | 2844.01 | 2863.56 | 2870.39 | 2402.62 | 2401.47 | 2420.26 | 2253.13 | 2256.69 | 2262.07
60F | 2800.5707 | 2615.2 | 2610.6 | 2613.43 | 2711.99 | 2714.27 | 2718.82 | 2819.77 | 2827.26 | 2847.01 | 2374.82 | 2382.42 | 2389.63 | 2216.29 | 2227.42 | 2237.34
70F | 3153.3507 | 2600.79 | 2606.46 | 2614.08 | 2690.37 | 2703.93 | 2709.76 | 2760.99 | 2770.28 | 2773.73 | 2300.38 | 2314.11 | 2330.77 | 2160.92 | 2168.23 | 2163.65

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2693.1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 487.84 | 487.41 | 3179.65 | 2682.34 | 1240.93 | FULL
G1 | 2697.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 487.26 | 486.85 | 3114.65 | 2687.5 | 1269.49 | FULL
G2 | 2701.5 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 488.23 | 487.79 | 3133.53 | 2690.54 | 1290.24 | FULL
G3 | 2785.86 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 487.07 | 486.68 | 3186.49 | 2773.68 | 1335.76 | FULL
G4 | 2797.47 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 487.28 | 486.92 | 3122.04 | 2786.23 | 1375.23 | FULL
G5 | 2798.68 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 486.96 | 486.58 | 3139.97 | 2787.38 | 1396.43 | FULL
G6 | 3042.25 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.38 | -196.81 | -130.93 | 3211.3 | 3027.17 | 1556.11 | FULL
G7 | 3057.47 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -11.14 | -130.44 | -134.36 | 3146.54 | 3042.52 | 1612.42 | FULL
G8 | 3056.3 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.38 | -196.71 | -130.38 | 3166.16 | 3041.5 | 1625.93 | FULL
G9 | 2514.11 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -11.42 | -88.66 | -138.1 | 3216.81 | 2504.49 | 1464.12 | FULL
G10 | 2520.43 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.96 | -160.72 | -138.97 | 3152.31 | 2510.57 | 1494.55 | FULL
G11 | 2521.71 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -11.42 | -88.44 | -138.18 | 3171.72 | 2511.48 | 1509.74 | FULL
G12 | 2496 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.81 | -509.48 | -508.67 | 3237.52 | 2486.96 | 1573.26 | FULL
G13 | 2505.31 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.81 | -509.75 | -508.9 | 3175.06 | 2496.06 | 1604.74 | FULL
G14 | 2516.82 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.81 | -508.31 | -507.6 | 3194.52 | 2507.77 | 1641.24 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2736.63 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 479.69 | 479.28 | 2519.79 | 2725.16 | 1297.02 | FULL
G1 | 2740.42 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 479.47 | 479.04 | 2456.14 | 2729.99 | 1325.72 | FULL
G2 | 2750.17 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 479.44 | 478.68 | 2473.45 | 2738.59 | 1360.26 | FULL
G3 | 2828.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 478.58 | 478.21 | 2526.92 | 2816.88 | 1398.09 | FULL
G4 | 2840.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 479.02 | 478.66 | 2463.39 | 2828.06 | 1436 | FULL
G5 | 2837.43 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 478.34 | 477.95 | 2482.6 | 2824.63 | 1452.75 | FULL
G6 | 2975.24 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -498.61 | -498.14 | 2545.41 | 2961.68 | 1579.43 | FULL
G7 | 2984.5 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -495.59 | -495.17 | 2482.73 | 2970.49 | 1609.42 | FULL
G8 | 2990.02 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -493.7 | -493.44 | 2503.11 | 2976.16 | 1624.97 | FULL
G9 | 2505.27 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -11.42 | -84.58 | -132.2 | 2554.03 | 2496.13 | 1498.64 | FULL
G10 | 2509.45 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -16.96 | -156.63 | -133.49 | 2492.75 | 2500.4 | 1509.33 | FULL
G11 | 2553.85 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.81 | -500.2 | -499.09 | 2512.04 | 2544.55 | 1576.94 | FULL
G12 | 2357.01 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -497.59 | -496.77 | 2574.16 | 2348.54 | 1536.93 | FULL
G13 | 2385.45 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.81 | -500.64 | -499.83 | 2512.82 | 2377.26 | 1570.16 | FULL
G14 | 2401.99 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.81 | -500.22 | -499.42 | 2532.49 | 2393.92 | 1611.31 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2668.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.74 | 444.36 | 2286.25 | 2657.59 | 1286.38 | FULL
G1 | 2672.9 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.71 | 444.32 | 2222.81 | 2662.33 | 1314.15 | FULL
G2 | 2682.47 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.68 | 444.33 | 2240.94 | 2672.09 | 1350.52 | FULL
G3 | 2762.68 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 443.91 | 443.5 | 2294.34 | 2751.43 | 1387.95 | FULL
G4 | 2761.49 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 443.79 | 443.38 | 2232.18 | 2750.61 | 1406.39 | FULL
G5 | 2778.09 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.4 | 444.04 | 2249.67 | 2766.33 | 1452.08 | FULL
G6 | 2855.82 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -486.92 | -486.64 | 2311.36 | 2844.01 | 1533.97 | FULL
G7 | 2875.93 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -488.9 | -488.68 | 2248.78 | 2863.56 | 1576.51 | FULL
G8 | 2883.09 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -487.82 | -487.57 | 2269.24 | 2870.39 | 1603.73 | FULL
G9 | 2410.78 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -489.43 | -489.32 | 2321.76 | 2402.62 | 1473.06 | FULL
G10 | 2410.38 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -490.79 | -490.45 | 2258.83 | 2401.47 | 1496.75 | FULL
G11 | 2428.64 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -487.16 | -486.79 | 2279.9 | 2420.26 | 1531.95 | FULL
G12 | 2261.16 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -491.06 | -490.13 | 2341.38 | 2253.13 | 1518.3 | FULL
G13 | 2263.66 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -491.29 | -490.96 | 2280.85 | 2256.69 | 1524.57 | FULL
G14 | 2269.71 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -488.84 | -488.53 | 2299.6 | 2262.07 | 1571.19 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2624.9 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 445.01 | 444.02 | 2812.85 | 2615.2 | 1236 | FULL
G1 | 2620.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.51 | 444.14 | 2749.35 | 2610.6 | 1251.99 | FULL
G2 | 2623.71 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 443.93 | 443.42 | 2766.73 | 2613.43 | 1279.85 | FULL
G3 | 2723.54 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.96 | 444.56 | 2820.34 | 2711.99 | 1339.34 | FULL
G4 | 2725.53 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.21 | 443.81 | 2757.04 | 2714.27 | 1366.48 | FULL
G5 | 2730.46 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.4 | 443.95 | 2774.39 | 2718.82 | 1394.36 | FULL
G6 | 2831.78 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -467.49 | -467.23 | 2837.03 | 2819.77 | 1496.25 | FULL
G7 | 2840.08 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -467.42 | -467.15 | 2773.45 | 2827.26 | 1525.58 | FULL
G8 | 2859.3 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -468.5 | -468.18 | 2792.11 | 2847.01 | 1563.45 | FULL
G9 | 2382.71 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -471.38 | -470.48 | 2847.18 | 2374.82 | 1425.55 | FULL
G10 | 2390.8 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -469.39 | -468.5 | 2783.89 | 2382.42 | 1455.01 | FULL
G11 | 2398.27 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -467.21 | -466.28 | 2803.41 | 2389.63 | 1483.72 | FULL
G12 | 2223.32 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -468.25 | -467.15 | 2865.04 | 2216.29 | 1468.08 | FULL
G13 | 2234.21 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -471.66 | -470.53 | 2803.81 | 2227.42 | 1476.5 | FULL
G14 | 2243.89 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -470.27 | -469.12 | 2821.94 | 2237.34 | 1517.81 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2611.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.31 | 444.04 | 3168.03 | 2600.79 | 1224.67 | FULL
G1 | 2617.07 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.05 | 444.02 | 3103.29 | 2606.46 | 1252.78 | FULL
G2 | 2623.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.65 | 444.3 | 3120.8 | 2614.08 | 1281.59 | FULL
G3 | 2701.1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 443.76 | 443.31 | 3175.57 | 2690.37 | 1317.21 | FULL
G4 | 2715.53 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.62 | 444.23 | 3111.05 | 2703.93 | 1357.74 | FULL
G5 | 2720.71 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 36.64 | 444.12 | 443.73 | 3128.57 | 2709.76 | 1384.7 | FULL
G6 | 2772.33 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -454.49 | -454.29 | 3189.28 | 2760.99 | 1460.62 | FULL
G7 | 2782.12 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -454.53 | -454.26 | 3125.2 | 2770.28 | 1490.82 | FULL
G8 | 2785.8 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -453.65 | -453.39 | 3144.33 | 2773.73 | 1515.78 | FULL
G9 | 2308.61 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -454.7 | -454.69 | 3198.74 | 2300.38 | 1374.52 | FULL
G10 | 2322.07 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -456.69 | -455.8 | 3134.97 | 2314.11 | 1413.95 | FULL
G11 | 2339.56 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -456.26 | -455.36 | 3154.75 | 2330.77 | 1443.53 | FULL
G12 | 2167.15 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -457.8 | -457.13 | 3217.29 | 2160.92 | 1433.59 | FULL
G13 | 2175.69 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -38.77 | -458.75 | -457.65 | 3154.81 | 2168.23 | 1447.44 | FULL
G14 | 2170.25 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.77 | -452.51 | -452.24 | 3173.58 | 2163.65 | 1470.54 | FULL
001R2WINTER09v5NSL