## 25F nomo
Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 002
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3320.2936
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3108.85 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2633.99 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 2762.01 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2779.14 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2633.99 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3011.94 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 3012.53 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2963.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2875.3 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 766.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2779.14 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2762.01 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 3308.15 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2875.3 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 3130.64 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3130.64 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 3011.94 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3058.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 3154.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 857.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3058.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3108.85 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 2963.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 3012.53 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 980.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3308.15 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 857.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3154.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 766.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 980.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 002
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2633.11
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2853.55 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2541.66 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 2702.13 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2699.48 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2541.66 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2909.47 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2979.18 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2186.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2843.08 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 32.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2699.48 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2702.13 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 3195.68 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2843.08 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 3048.79 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3048.79 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2909.47 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2290.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2395.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 114.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2290.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2853.55 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 2186.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2979.18 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 222.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3195.68 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 114.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2395.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 32.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 222.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 002
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2437.8085
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2822.15 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2479.79 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 2644.78 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2622.46 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2479.79 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2855.64 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2960.06 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1208.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2787.57 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -1160.54 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2622.46 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2644.78 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 3200.25 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2787.57 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 3020.58 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3020.58 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2855.64 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1310.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1414.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -1021.64 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1310.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2822.15 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1208.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2960.06 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | -991.04 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3200.25 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | -1021.64 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1414.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -1160.54 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -991.04 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 002
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2969.9892
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2743.47 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2420.91 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 2586.58 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2557.59 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2420.91 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2794.9 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2886.19 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1651.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2727.38 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -536.36 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2557.59 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 2586.58 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 3041.33 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2727.38 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2946.95 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2946.95 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2794.9 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1742.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1865.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -498.9 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1742.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2743.47 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1651.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2886.19 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | -444.92 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3041.33 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | -498.9 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1865.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -536.36 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -444.92 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 002
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3267.64
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2537.46 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2416.98 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 2577.5 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2577.22 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2416.98 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2810.66 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2739.11 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 1726.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2675.19 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -456.06 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2577.22 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2577.5 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 2958.69 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2675.19 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2918.61 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2918.61 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2810.66 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1828.44 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1940.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -361.58 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1828.44 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2537.46 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1726.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2739.11 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -315.19 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2958.69 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -361.58 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1940.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -456.06 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -315.19 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
G0 | 3108.85 | 2853.55 | 2822.15 | 2743.47 | 2537.46
G1 | 2762.01 | 2702.13 | 2644.78 | 2586.58 | 2577.5 | Season/Year: | WINTER 2009
G2 | 2633.99 | 2541.66 | 2479.79 | 2420.91 | 2416.98 | Direction: | South-to-North (SN)
G3 | 3012.53 | 2979.18 | 2960.06 | 2886.19 | 2739.11 | Case Loads: | Light Loads
G4 | 2875.3 | 2843.08 | 2787.57 | 2727.38 | 2675.19 | Outage: | 002
G5 | 2779.14 | 2699.48 | 2622.46 | 2557.59 | 2577.22 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3308.15 | 3195.68 | 3200.25 | 3041.33 | 2958.69 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3130.64 | 3048.79 | 3020.58 | 2946.95 | 2918.61 | Study Person: | JGO7470
G8 | 3011.94 | 2909.47 | 2855.64 | 2794.9 | 2810.66 | Source: | 002WINTER09v2SNL(SN@100MW)
G9 | 3154.14 | 2395.83 | 1414.63 | 1865.03 | 1940.3
G10 | 3058.54 | 2290.22 | 1310.09 | 1742.79 | 1828.44
G11 | 2963.81 | 2186.77 | 1208.6 | 1651.91 | 1726.28
G12 | 980.15 | 222.55 | -991.04 | -444.92 | -315.19
G13 | 857.45 | 114.38 | -1021.64 | -498.9 | -361.58
G14 | 766.86 | 32.32 | -1160.54 | -536.36 | -456.06
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Light Loads |  |  | 002 | Bothell - Horse Ranch Tap section of Sedro Woolley - Bothell - Horse Ranch 230kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3320.2936 | 3109.5 | 2761.74 | 2633.85 | 3013.66 | 2875.03 | 2778.13 | 3307.96 | 3130.21 | 3011.58 | 3154.31 | 3058.31 | 2964.11 | 978.98 | 856.67 | 765.86
35F | 2633.11 | 2853.14 | 2701.88 | 2540.58 | 2978.79 | 2842.02 | 2698.28 | 3195.24 | 3048.39 | 2908.47 | 2394.23 | 2289.84 | 2186.08 | 220.98 | 114.13 | 31.94
45F | 2437.8085 | 2821.91 | 2643.9 | 2478.08 | 2959.76 | 2786.57 | 2623.43 | 3199.97 | 3020.25 | 2855.53 | 1414.12 | 1310.23 | 1208.54 | -989.69 | -1022.29 | -1161.38
60F | 2969.9892 | 2743.16 | 2584.42 | 2420.62 | 2885.92 | 2726.57 | 2556.44 | 3041 | 2946.67 | 2795.82 | 1863.18 | 1742.04 | 1651.1 | -445.62 | -498.23 | -536.92
70F | 3267.64 | 2537.42 | 2576.72 | 2416.66 | 2739.03 | 2674.83 | 2577.15 | 2958.51 | 2919.9 | 2810.55 | 1939.47 | 1825.71 | 1725.26 | -315.34 | -362.33 | 629.49

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3108.85 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -15.9 | -512.58 | -512.45 | 3396.25 | 3109.5 | -2005.17 | CTG_FAIL_IN_FULL
G1 | 2762.01 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -488.82 | -489.14 | 3310.65 | 2761.74 | -1766.87 | FULL
G2 | 2633.99 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -492.36 | -492.16 | 3313.96 | 2633.85 | -1663.95 | FULL
G3 | 3012.53 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -477.84 | -477.6 | 3390.48 | 3013.66 | -1873.88 | FULL
G4 | 2875.3 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -485.4 | -485.09 | 3310.38 | 2875.03 | -1770.31 | FULL
G5 | 2779.14 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -494.5 | -494.31 | 3315.62 | 2778.13 | -1674.86 | FULL
G6 | 3308.15 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -482.23 | -482.57 | 3393.06 | 3307.96 | -1921.44 | FULL
G7 | 3130.64 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -486.67 | -487.03 | 3313 | 3130.21 | -1789.31 | FULL
G8 | 3011.94 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -493.09 | -493.48 | 3316.31 | 3011.58 | -1693.9 | FULL
G9 | 3154.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -476.34 | -476.31 | 3369.63 | 3154.31 | -1614.68 | FULL
G10 | 3058.54 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -475.47 | -475.44 | 3295.3 | 3058.31 | -1532.11 | FULL
G11 | 2963.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -473.2 | -473.14 | 3304.94 | 2964.11 | -1445.74 | FULL
G12 | 980.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -453.68 | -453.66 | 3322.61 | 978.98 | -195.43 | FULL
G13 | 857.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -452.92 | -452.9 | 3256.27 | 856.67 | -100.05 | FULL
G14 | 766.86 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -453.4 | -453.39 | 3271.9 | 765.86 | -21.35 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2853.55 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -474.49 | -474.66 | 2699.58 | 2853.14 | -1786.44 | FULL
G1 | 2702.13 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -480.6 | -480.93 | 2620.96 | 2701.88 | -1675.35 | FULL
G2 | 2541.66 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -484.28 | -484.39 | 2627.27 | 2540.58 | -1554.77 | FULL
G3 | 2979.18 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -474.2 | -473.81 | 2700.63 | 2978.79 | -1787 | FULL
G4 | 2843.08 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -480.86 | -481.1 | 2621.98 | 2842.02 | -1690.65 | FULL
G5 | 2699.48 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -485.76 | -485.54 | 2627.44 | 2698.28 | -1580.16 | FULL
G6 | 3195.68 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -473.75 | -474.09 | 2701.16 | 3195.24 | -1807.99 | FULL
G7 | 3048.79 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -478.91 | -478.63 | 2624.46 | 3048.39 | -1683.15 | FULL
G8 | 2909.47 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -485.82 | -486 | 2629.65 | 2908.47 | -1572.9 | FULL
G9 | 2395.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -457.75 | -457.66 | 2661.69 | 2394.23 | -1114.16 | FULL
G10 | 2290.22 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -455.83 | -455.73 | 2591.31 | 2289.84 | -1029.06 | FULL
G11 | 2186.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -453.78 | -453.67 | 2603.14 | 2186.08 | -946.01 | FULL
G12 | 222.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -444.73 | -444.84 | 2650.27 | 220.98 | 285.09 | FULL
G13 | 114.38 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -445.5 | -445.4 | 2586.67 | 114.13 | 372.11 | FULL
G14 | 32.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -446.77 | -446.72 | 2604.76 | 31.94 | 445.15 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2822.15 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -461.71 | -462.1 | 2453.36 | 2821.91 | -1735.61 | FULL
G1 | 2644.78 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -465.4 | -465.74 | 2376.12 | 2643.9 | -1607.66 | FULL
G2 | 2479.79 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -467.87 | -467.95 | 2381.75 | 2478.08 | -1484.53 | FULL
G3 | 2960.06 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -462.06 | -462.54 | 2454.47 | 2959.76 | -1749.35 | FULL
G4 | 2787.57 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -466.5 | -466.75 | 2377.5 | 2786.57 | -1622.42 | FULL
G5 | 2622.46 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -468.2 | -468.08 | 2382.96 | 2623.43 | -1502.44 | FULL
G6 | 3200.25 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -462.4 | -462.09 | 2456.19 | 3199.97 | -1770.79 | FULL
G7 | 3020.58 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -465.49 | -465.72 | 2379.64 | 3020.25 | -1635.81 | FULL
G8 | 2855.64 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -468.1 | -467.73 | 2385.08 | 2855.53 | -1514.12 | FULL
G9 | 1414.63 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -410.76 | -410.69 | 2403.01 | 1414.12 | -519.89 | FULL
G10 | 1310.09 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -410.07 | -410.02 | 2335.54 | 1310.23 | -433.15 | FULL
G11 | 1208.6 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -409.65 | -409.61 | 2350.66 | 1208.54 | -348.34 | FULL
G12 | -991.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.95 | -423.29 | -423.29 | 2430 | -989.69 | 993.34 | FULL
G13 | -1021.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.95 | -425.37 | -425.25 | 2367.43 | -1022.29 | 1039.11 | FULL
G14 | -1160.54 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.95 | -424.21 | -424.12 | 2387.76 | -1161.38 | 1135.16 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2743.47 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -436.88 | -436.35 | 2981.27 | 2743.16 | -1729.74 | FULL
G1 | 2586.58 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -438.71 | -438.47 | 2902.9 | 2584.42 | -1611.78 | FULL
G2 | 2420.91 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -443.06 | -442.91 | 2908.94 | 2420.62 | -1489.29 | FULL
G3 | 2886.19 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -438.06 | -437.89 | 2983.21 | 2885.92 | -1739.65 | FULL
G4 | 2727.38 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -439.63 | -439.29 | 2903.86 | 2726.57 | -1628.24 | FULL
G5 | 2557.59 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -443.28 | -443.35 | 2909.81 | 2556.44 | -1501.09 | FULL
G6 | 3041.33 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -434.49 | -434.58 | 2984.34 | 3041 | -1723.57 | FULL
G7 | 2946.95 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -440.35 | -440.62 | 2906.08 | 2946.67 | -1634.75 | FULL
G8 | 2794.9 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -443.18 | -442.84 | 2912.18 | 2795.82 | -1512.19 | FULL
G9 | 1865.03 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -418.42 | -418.36 | 2936.87 | 1863.18 | -817.14 | FULL
G10 | 1742.79 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -415.01 | -414.88 | 2867.23 | 1742.04 | -716.69 | FULL
G11 | 1651.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -415.43 | -415.37 | 2879.99 | 1651.1 | -642.7 | FULL
G12 | -444.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.95 | -416.78 | -416.75 | 2943.23 | -445.62 | 650.82 | FULL
G13 | -498.9 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.95 | -418.47 | -418.36 | 2878.88 | -498.23 | 709.56 | FULL
G14 | -536.36 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.95 | -420.33 | -420.37 | 2897.16 | -536.92 | 758.15 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2537.46 | Branch HORSRNCH (42320) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 16.91 | 562.02 | 561.78 | 3331.31 | 2537.42 | -1614.53 | FULL
G1 | 2577.5 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -424.09 | -424.33 | 3258.92 | 2576.72 | -1609.33 | FULL
G2 | 2416.98 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -425.53 | -425.31 | 3264.5 | 2416.66 | -1484.67 | FULL
G3 | 2739.11 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.04 | -2197.6 | -2196.33 | 3336.21 | 2739.03 | -1671.86 | FULL
G4 | 2675.19 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -419.87 | -420.05 | 3259.87 | 2674.83 | -1601.03 | FULL
G5 | 2577.22 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -16.59 | -429.78 | -429.67 | 3265.19 | 2577.15 | -1509.69 | FULL
G6 | 2958.69 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.04 | -2174.01 | -2173.3 | 3334.15 | 2958.51 | -1674.7 | FULL
G7 | 2918.61 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -422.37 | -422.77 | 3261.62 | 2919.9 | -1624.04 | FULL
G8 | 2810.66 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -16.59 | -427.49 | -427.27 | 3266.65 | 2810.55 | -1529.49 | FULL
G9 | 1940.3 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -417.86 | -417.77 | 3294.12 | 1939.47 | -861.98 | FULL
G10 | 1828.44 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -416.14 | -416.06 | 3223.64 | 1825.71 | -769.48 | FULL
G11 | 1726.28 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.35 | -414.96 | -414.87 | 3236.02 | 1725.26 | -687.15 | FULL
G12 | -315.19 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.95 | -416.8 | -416.73 | 3295.98 | -315.34 | 575 | FULL
G13 | -361.58 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.95 | -418.62 | -418.85 | 3231.39 | -362.33 | 629.49 | FULL
G14 | -456.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.95 | -418.91 | -418.88 | 3249.87 | -456.29 | 708.62 | FULL
002WINTER09v2SNL(SN@100MW)