# Review of ESPC M&V Plan for GSA Piscataway Federal Center, Piscataway, NJ

## Section 1: Background

This review of the M&V plan for this ESPC project was performed to ensure:

M&V conforms to agreed-upon risk allocation;

M&V is adequate for all significant savings streams;

The baseline is adequately defined;

The savings estimates are sound & reasonable;

Performance period activities are meaningful and adequate to support the guarantee;

Overall project assumptions are reasonable.

Table 1: Summary of Project Data

| Project name: | GSA Piscataway Federal Center |
| --- | --- |
| Location: | Piscataway, NJ |
| Delivery Order #: | FAKE34621 |
| Date of proposal: | April 1, 2003 |

Table 2: Summary of Review Distribution

| Reviewer: | Lia Webster |
| --- | --- |
| Reviewer Contact Information: | Project Manager, Nexant, Inc. 1401 Walnut St, Boulder CO 80302 303.402.2493 lwebster@nexant.com |
| Date of Review: | May 6, 2005 |
| Agency Contact info: | Richard Handy Sr. Engineer Dept of General Services 1800 Highrise Rd, Piscataway NJ 10012 201.455.3667 rihandy@piscataway.gsa.gov |
| Date review was provided to Agency contact: | May 6, 2005 |
| DOE Contact info: | Paul King DOE Outreach/Technical Assistance 617-565-9712 paul.king@ee.doe.gov |
| Date review was provided to DOE contact: | May 6, 2005 |

## Section 2: Summary of Findings

In general, this M&V plan is very robust and will accurately quantify energy and cost savings for this project. Some minor items need to be updated for consistency and clarity, as outlined below.

### Whole Project

Requirements for government witnessing of measurement in the baseline and performance period are not included and should be defined.

Plan presented for dispute resolution is not very specific and should be enhanced.

### ECM 1 – Lighting Retrofit

Note government’s involvement with collection and verification of baseline data if appropriate.

Complete baseline and post-installation energy and cost data in Table 3-2.

### ECM 2 – Energy Management and Control System (EMCS)

Add back-up information on chiller energy use and savings from implementing improved controls after hours. Consider adding after hours run-time check using EMCS data to validate these savings.

Define roles for ESCO and GSA to manage EMCS data.

### ECM 3 – Chiller Replacement

Specify performance parameters for the new chiller, such as chilled water flow and supply temperature. It may also be appropriate for ESCO to specify cooling tower performance requirement

Note government’s involvement with collection and verification of baseline data if appropriate.

Remove statement in Section 5.7 that places repair responsibility of the chiller with GSA so it is consistent with Risk Matrix.

Provide back-up data on source of minimum ton-hours. Clarify how this data will be applied to the savings calculation method.

## Section 3: Review of Individual Measures

Table 3: Summary of Savings from Proposed ECMs

| ECM # | ECM Name / Description | Annual Energy & Water Cost Savings ($) | Annual O&M Cost Savings ($) | % Total Savings | % Total Energy & Water Savings |
| --- | --- | --- | --- | --- | --- |
| 96 | Lighting | $14,811 | $0 | 15% | 18% |
| 2 | EMCs | $47,211 | $0 | 49% | 56% |
| 3 | Chiller | $22,561 | $12,000 | 36% | 27% |
|  | Totals: | $84,583 | $12,000 | $96,583 |  |

Table 4: Summary of M&V and Savings Calculation Methods

| ECM # | M&V Method from FEMP Guideline | Baseline Determination Methodology | Post-install and Performance Period M&V & Savings Calculations |
| --- | --- | --- | --- |
| 1 | A (LE-A-01) | Stipulated fixture wattages; short-term monitoring of operating hours on a statistically valid sample of fixtures | Adjust fixture counts and energy use based on as-built data |
| 2 | B (GLV-B-01) | Instantaneous power measurements; stipulated baseline operating hours, | Monitored post-installation operating hours |
| 3 | B (CH-B-02) | Metered baseline chiller performance to develop model | Meter new chiller kW and Tons, predict baseline kW |

### Review of ECM 1: Lighting Retrofit

| Annual Cost Savings: | $14,811 |
| --- | --- |
| O&M Cost savings: | $0 |
| % Total Project Cost savings: | 15% |

#### ECM Specific Comments

This M&V plan is based on LE-A-02 from the FEMP M&V Guideline and is very robust for this ECM. Operating hours were measured, including coincident operation to determine demand savings. The only risk is that the existing lighting equipment was properly defined, since the power use is based on this information.

Government witnessing of baseline data was not noted.

Energy and cost data is missing from Table 3-2: Proposed Annual Savings For ECM-1.

#### ECM Specific Recommendations

Note government’s involvement with collection and verification of baseline data if appropriate.

Complete baseline and post-installation energy and cost data in Table 3-2.

### Review of ECM 2: Installation of Energy Management and Control System (EMCS)

| Annual Cost Savings: | $47,211 |
| --- | --- |
| O&M Cost savings: | $0 |
| % Total Project Cost savings: | 49% |

#### ECM Specific Comments

After-hours chiller savings are stipulated based on broad assumptions and is not well documented.

Other electrical savings resulting from this measure are being accurately calculated, assuming baseline operating hours are as defined. Natural gas savings are not quantified, although cost savings will result.

Data management for the data recorded by the EMCS has not been adequately defined for this measure. It is unclear who will manage data – how it will be saved, backed-up and transferred to the ESCO.

#### ECM Specific Recommendations

Add back-up information on chiller energy use and savings from implementing improved controls after hours. Consider adding after hours run-time check using EMCS data to validate these savings.

Define roles for ESCO and GSA to manage EMCS data.

### Review of ECM 3: Chiller Replacement

| Annual Cost Savings: | $34,561 |
| --- | --- |
| O&M Cost savings: | $12,000 |
| % Total Project Cost savings: | 36% |

#### ECM Specific Comments

This M&V plan is based on FEMP M&V method CH-B-02 and is very robust. Baseline and post-installation performance data is metered.

No performance parameters for the chiller operation have been defined.

Government witnessing of baseline data was not noted.

No specification was provided for the ultrasonic flow meter used in the baseline measurements.

Baseline and post-install electric demand are not included in Table 5-1.

Repair responsibility for the chiller described in the M&V plan is not consistent with risk and responsibility matrix. Based on the O&M plan, ABC Engineering should maintain responsibility for the chiller.

Minimum ton-hours are set for operation of the chiller that will be used to calculate savings in case chiller use decreases dramatically. The source for these minimum ton-hours is not included, and enough data is not provided to apply savings calculations.

#### ECM Specific Recommendations

Specify performance parameters for the new chiller, such as chilled water flow and supply temperature. It may also be appropriate for ESCO to specify cooling tower performance requirement

Note government’s involvement with collection and verification of baseline data if appropriate.

Remove statement in Section 5.7 that places repair responsibility of the chiller with GSA so it is consistent with Risk Matrix.

Provide back-up data on source of minimum ton-hours. Clarify how this data will be applied to the savings calculation method.

## Section 4: M&V Plan and Savings Calculation Methods  - Content Checklists (v. 1.0)

### Project Level Checklist

| Value Level | Item | Included? Note any deficiencies |
| --- | --- | --- |
| 1. Executive Summary / M&V Overview & Proposed Savings Calculations |
| 1.1 Proposed Annual Savings Overview |
| High | Table showing the projected savings by ECM broken out by O&M savings, energy units, energy cost, and other savings values as applicable. Include all applicable fuels / commodities for project, such as: electric energy, electric demand, natural gas, fuel oil, coal, water, etc. | Table 1-1 |
| High | First Year Guaranteed Cost Savings | See DO-1 |
| Optional | Site Use and Savings Overview - Include approximate % total site usage saved (for year 1) by energy source type for site (optional) | Electrical cost only; ~10% reduction |
| 1.2 M&V Plan Summary |
| Medium | Table presenting M&V Option (from M&V guideline) used and summary of M&V approach for each ECM | Table 1-3 |
| 2. Whole Project Data / Global Assumptions |
| 2.1 Risk & Responsibility |
| High | Summarize allocation of responsibility for key items related to M&V. | Attached |
| Medium | Reference location of Risk & Responsibility Matrix (if required). |  |
| 2.2 Energy, Water, and Operations & Maintenance (O&M) Rate Data |
| High | Details of baseline energy and water rates included | Yes |
| High | Provide performance period rate adjustment factors for energy, water, and O&M cost savings, if used. | None used |
| 2.3 Schedule & Reporting for Verification Activities |
| Medium | Define requirements for witnessing of measurements during: | Not INCLUDED |
|  | Baseline development |  |
|  | Post-installation verification activities |  |
|  | Performance period |  |
| Medium | Define schedule of verification reporting activities, including: |  |
|  | Post-Installation Report | Yes |
|  | Annual Report | Yes |
| Medium | Define content and format of reports: |  |
|  | Post-installation report (Use Post-Installation Report Outline.) | IDIQ referenced |
|  | Annual M&V reports (Use Annual Report Outline) | IDIQ referenced |
|  | Interval M&V reports (Develop report outline if needed) | None proposed |
| 2.4 Operations, Preventive Maintenance, Repair, and Replacement Reporting Requirements |
| High | Define Government and ESCO reporting requirements: | ESCO only |
|  | Summarize key verification activities and reporting responsibilities of government and ESCO on operations, preventive maintenance, repair, and replacement items from details in ECM specific M&V Plans. |  |
|  | Define content of reports and reporting schedule. | Yes |
| 2.5 Construction Period Savings |
| High | Provide overview of how construction period savings will be calculated, if applicable. | None claimed |
| 2.6 Status of Rebates |
| Medium | Provide a summary of the source of any third-party rebates or incentives provided on this project. | None |
|  | Provide status of any third-party rebates or incentives. |  |
| 2.7 Dispute Resolution |
| Medium | Describe plan for resolving disputes regarding issues such as baseline, baseline adjustment, energy savings calculation, and the use of periodic measurements. | weak plan |

### ECM Level Checklist

| Value Level | Item | Included? Note any deficiencies |
| --- | --- | --- |
|  |  | ECM 1: Lighting | ECM 2: EMCS | ECM 3: Chiller |  |  |
|  | % Project Total Cost Savings: | 15% | 49% | 36% |  |  |
|  | % Project Energy & Water Cost Savings: | 18% | 56% | 27% |  |  |
| 3. ECM [Name / #] M&V Plan and Savings Calculation Methods |
| 3.1 Overview of ECM, M&V Plan, and Savings Calculation for ECM |
| High | Summarize the scope of work, location, and how cost savings are generated. | Yes | Yes | Yes |  |  |
|  | Describe source of all savings including energy, water, O&M, and other (if applicable). | Yes | Yes | Yes |  |  |
| Medium | Specify the M&V guideline and option used | Yes | Yes | Yes |  |  |
| High | Provide an overview of M&V Activities for ECM. | Yes | Yes | Yes |  |  |
|  | Explain intent of M&V plan, including what is being verified. | Yes | Yes | Yes |  |  |
| High | Provide an overview of savings calculations methods for ECM. | Yes | Yes | Yes |  |  |
|  | Provide a general description of analysis methods used for savings calculations. | Yes | Yes | Yes |  |  |
| 3.2 Energy and Water Baseline Development |
| High | Describe in general terms how the baseline for this ECM is defined. | Yes | Yes | Yes |  |  |
| High | Describe variables affecting baseline energy or water use. | Yes | Yes | Yes |  |  |
|  | Include variables such as weather, operating hours, set point changes, etc. | Yes | Yes | Yes |  |  |
| HIGH | Describe how each variable will be quantified, i.e. measurements, monitoring, assumptions, manufacturer data, maintenance logs, engineering resources, etc. | Yes | Yes | Yes |  |  |
| High | Define key system performance factors characterizing the baseline conditions such as comfort conditions, lighting intensities, temperature set points, etc | Yes | Yes | NO! |  |  |
| Medium | Define requirements for government witnessing of measurements if different than whole project data requirements included in Section 2.3. | NOT Included! | NOT Included! | NOT Included! |  |  |
| High | Provide details of baseline data collected, including: |  |  |  |  |  |
|  | Parameters monitored/measured | Yes | Yes | Yes |  |  |
|  | Details of equipment monitored, i.e. location, type, model, quantity, etc. | Yes | Yes | Yes |  |  |
| Medium | Sampling plan, including details of usage groups and sample sizes | YES | N/A | N/A |  |  |
| Medium | Duration, frequency, interval, and seasonal or other requirements of measurements | Yes | N/A | N/A |  |  |
| Medium | Personnel, dates, and times of measurements | NO! | Yes | No |  |  |
|  | Proof of government witnessing of measurements (if required) | NO! | Yes | No |  |  |
| Low | Monitoring equipment used | Yes | Yes | Yes |  |  |
|  | Installation requirements for monitoring equipments (test plug for temperature sensors, straight pipe for flow measurement, etc.) | No | No | No – need ultra sonic flow meter spec |  |  |
|  | Certification of calibration / calibration procedures followed | No | Yes | Yes except above |  |  |
|  | Expected accuracy of measurements/monitoring equipment | Yes | Yes | Yes except above |  |  |
| Medium | Quality control procedures used | Yes | No | No |  |  |
| Medium | Form of data (.xls, .cvs, etc.) | Yes | Yes | Yes |  |  |
| HIGH | Results of measurements (attach appendix and electronic forma as necessary) |  | Need chiller backup data |  |  |  |
| Medium | Completed data collection forms, if used | NA | Yes | NA |  |  |
| High | Provide details of baseline data analysis performed, including: |  |  |  |  |  |
|  | Analysis using results of measurements | Yes | Need off hours chiller calc backup | Yes |  |  |
|  | Weather normalized regressions | NA | NA | NA |  |  |
|  | Weather data used and source of data | NA | NA | NA |  |  |
| 3.3 Proposed Energy & Water Savings Calculations and Methodology |
| High | Provide detailed description of analysis methodology used. | Okay | Okay | Okay |  |  |
|  | Describe any data manipulation or analysis that was conducted prior to applying savings calculations. | Yes | Yes | Yes |  |  |
| High | Detail all assumptions and sources of data, including all stipulated values used in calculations. | Yes | Need better reference for Chiller model source | Yes |  |  |
| High | Include equations and technical details of all calculations made. (Use appendix and electronic format as necessary.) Include description of data format (headings, units, etc.). | Yes | Yes | Yes |  |  |
| High | Details of any savings or baseline adjustments that may be required | NA | None | None |  |  |
| High | Detail energy and water rates used to calculate cost savings. | Yes | Yes | Yes |  |  |
|  | Provide performance period energy and water rate adjustment factors, if different from in section 2.2.2. | Not used | Not used | Not used |  |  |
| 3.4 Operations and Maintenance and Other Cost Savings |
| High | Provide justification for O&M cost savings, if applicable | None | None | Yes |  |  |
|  | Describe how savings are generated | None | None | Yes |  |  |
|  | Detail cost savings calculations. | None | None | Yes |  |  |
|  | Provide performance period O&M cost savings adjustment factors, if different from in section 2.2.2. | None | None | NA |  |  |
| High | Provide justification for other cost savings, if applicable. | NA | NA | NA |  |  |
|  | Describe how savings are generated. | NA | NA | NA |  |  |
|  | Detail cost savings calculations. | NA | NA | NA |  |  |
|  | Provide performance period adjustment factors, if different from in section 2.2.2. | NA | NA | NA |  |  |
| 3.5 Proposed Annual Savings For ECM |
| HIGH | Table detailing proposed annual savings for this energy conservation measure for performance period: including the baseline energy use, post-install energy use, and projected savings for ECM. Detail energy units, energy cost, O&M savings, and other savings values as applicable. Include all applicable fuels / commodities for project, such as: electric energy, electric demand, natural gas, fuel oil, coal, water, etc. | Yes | Yes | Yes |  |  |
| 3.6 Post-Installation M&V Activities |
| High | Describe the intent of post-installation verification activities, including what will be verified. | Yes | Yes | Yes |  |  |
| High | Describe variables affecting post-installation energy or water use. | Yes | Yes | Yes |  |  |
| High | Include variables such as weather, operating hours, set point changes, etc. | Yes | Yes | Yes |  |  |
| HIGH | Describe how each variable will be quantified, i.e. measurements, monitoring, assumptions, manufacturer data, maintenance logs, engineering resources, etc. | Yes | Yes | Yes |  |  |
| High | Define key system performance factors characterizing the post-installation conditions such as lighting intensities, temperature set points, etc. | Yes | Needed? | NO! Needed |  |  |
| Medium | Define requirements for government witnessing of measurements if different than whole project data requirements included in Section 2.3. | None defined | None defined | None defined |  |  |
| HIGH | Provide details of post-installation data to be collected, including: | Yes | Yes | Yes |  |  |
|  | Parameters to be monitored | NA | Yes | Yes |  |  |
|  | Details of equipment to be monitored (location, type, model, quantity, etc.) | NA | Yes | Yes |  |  |
| High | Sampling plan, including details of usage groups and sample sizes | NA | Yes | Yes |  |  |
|  | Duration, frequency, interval, and seasonal or other requirements of measurements | NA | Yes | Yes |  |  |
| Low | Monitoring equipment to be used | NA | Yes | Yes |  |  |
|  | Installation requirements for monitoring equipment | NA | NA | NA |  |  |
|  | Calibration requirements / procedures | NA | Yes | Yes |  |  |
|  | Expected accuracy of measurements/monitoring equipment | NA | Yes | Yes |  |  |
| Medium | Quality control procedures to be used | NA | Yes | Yes |  |  |
| Medium | Form of data to be collected (.xls, .cvs, etc.) | NA | Yes | Yes |  |  |
| Medium | Sample data collection forms (optional) | NA | No | Yes |  |  |
| High | Detail data analysis to be performed | NA | Yes | Yes |  |  |
| 3.7 Performance Period Verification Activities |
| High | Describe variables affecting performance period energy or water use. | Yes | Yes | Yes |  |  |
|  | Include variables such as weather, operating hours, set point changes, etc. | Yes | Yes | Yes |  |  |
| HIGH | Describe how each variable will be quantified, i.e. measurements, monitoring, assumptions, manufacturer data, maintenance logs, engineering resources, etc. | Yes | Yes | Yes |  |  |
| High | Define key system performance factors characterizing the performance period conditions such as comfort conditions, lighting intensities, temperature set points, etc | Yes | Yes | NO – Need to define system op parameters |  |  |
| HIGH | Describe the intent of performance period verification activities – what will be verified. | Yes | Yes | Yes |  |  |
| Medium | Provide detailed schedule of performance period verification activities and inspections. | Yes | Yes | Yes |  |  |
| Medium | Define requirements for government witnessing of measurements if different than whole project data requirements included in Section 2.3. | None defined | None defined | None defined |  |  |
| HIGH | Provide details of performance period data to be collected, including: | Yes | Yes | Yes |  |  |
|  | Parameters to be monitored | NA | Yes | Yes |  |  |
|  | Details of equipment to be monitored (location, type, model, quantity, etc.) | NA | Yes | Yes |  |  |
| High | Sampling plan, including details of usage groups and sample sizes | NA | Yes | Yes |  |  |
|  | Duration, frequency, interval, and seasonal or other requirements of measurements | NA | Yes | Yes |  |  |
| Low | Monitoring equipment to be used | NA | Yes | Yes |  |  |
|  | Installation requirements for monitoring equipment | NA | No | Yes |  |  |
|  | Calibration requirements/procedures | NA | No | Yes |  |  |
|  | Expected accuracy of measurements/monitoring equipment | NA | No | Yes |  |  |
| Medium | Quality control procedures to be used | NA | No | Yes |  |  |
| Medium | Form of data to be collected (.xls, .cvs, etc.) | NA | No | Yes |  |  |
| Optional | Sample data collection forms (optional) | NA | No | Yes |  |  |
| High | Detail data analysis to be performed | None scheduled | Yes | Yes |  |  |
| High | Define operations, preventive maintenance, repair, and replacement reporting requirements. | ? | ? | ? |  |  |
|  | Detail verification activities and reporting responsibilities of government and ESCO on operations, preventive maintenance, repair, and replacement items. | None | None | Yes |  |  |
|  | Define contents of report and reporting schedule, if different than in global section 2.4. | None | None | None |  |  |