MuTr Response to Alarms in 1008 PROCEDURE

PHENIX Procedure No. PP-2.5.2.12-10

Revision:A									Date: 12-19-00

Hand Processed Changes

HPC No.			Date			Page Nos.			Initials

______________			______________		______________			______________

______________			______________		______________			______________

______________			______________		______________			______________

Approvals

______________________________			__________________________________________

PHENIX S E & I	Date				Cognizant Scientist/Engineer	Date

/Activity Manager

______________________________			__________________________________________

PHENIX Safety	Date				C-AD SAFETY			Date

______________________________ 			___________________________________________

1.0	Purpose and Scope

This procedure describes the steps that watch people should follow when the South Muon Tracking system is in operation.

- Watch Procedures

The CCAS watch or PHENIX people on shift should check the alarm panel located in the PHENIX Control Room.  The alarms that are associated only with the Muon Tracker are as follows:

Window Box A:

- 1-4 	MuTr South High Level Smoke

- 2-4	MuTr South Low/Mid Level smoke

- 3-4	MuTr South Smoke Detector Trouble

- 4-1	South Muon Main Power Breaker Trip

- 4-2	South Muon Main Power Breaker Fail

- 4-4	MuTr South Smoke Detector Isolated

- 5-8	MuTr South Water Leak Detected

Window Box B:

- 1-1	Electronics Racks Smoke Detected

- 1-2	Electronics Racks/TOF Smoke Detected

- 2-1	Electronics Racks Heat Detected

- 3-1	Electronics Racks Water Detected

- 3-4	Detector water Hi Temp/Makeup

- 4-2	VESDA Power Supply Trouble

- 5-4	Magnet Water Flow Low

If any of the above alarms are noted the watch person should:

- Note the alarms in the shift log book located next to the alarm panel.

- Hit the Acknowledge button

- If the alarm clears (signified by a warbling tone and a flashing window), hit the RESET button.

- If the alarm did not clear, call the appropriate person(s) on the on-call list until you reach someone.

The following alarms should be ignored as they will not be in operation during this running period or are of no consequence:

Window Box A:

- 1-6	East or West Carriage high level gas

- 1-7	GMH high level gas

- 2-6	Carriage low level gas

- 2-7	GMH low level gas

- 3-6	Carriage Gas Detector Malfunction

- 3-7	GMH Gas Detector Malfunction

- 4-6	IR Return Air High Level Gas

- 5-6	IR (PASS)floor high level gas

- 6-6	IR return air gas detector malfunction

- 6-7	IR HVAC/Vent fans off

- 6-8	PHENIX Bypass Active

Window Box B:

- 6-2	TOF Blowers Trouble

- 6-4	Power Supply water flow low

- Responsibilities

The on-call people responsible for the MuTr system are:

John Haggerty	689-2991

Paul Giannotti	821-3486 or 315-568-8480

Frank Toldo	732-5950

Ming Liu		924-7417