July 22, 1994

Contract #TW0592

SPECIAL SPECIFICATION

SECTION 13007

CLEAN ROOM CLEANING PROCEDURES

Page

PART 1 - GENERAL

1.01  Contents.	2

1.02  Work Included.	2

1.03  Responsibilities.	3

1.04  Related Sections.	3

1.05  Quality Assurance	4

1.06  Submittals, Samples, and Method Statements.	4

PART 2 - PRODUCTS

2.01  Materials And Equipment.	6

2.02  Cleaning Solutions.	7

PART 3 - EXECUTION

3.01  Cleaning Procedures.	8

SPECIAL SPECIFICATION

SECTION 13007

CLEAN ROOM CLEANING PROCEDURES

PART 1 - GENERAL

1.01  CONTENTS

A.  	Work Included.

B.  		Responsibilities

C.  		Related Work.

D.  		Quality Assurance.

E.  		Submittals, Samples, and Method Statements.

F.  		Cleaning Procedures.

1.  	Stage 1.

2.  	Stage 2.

3.  	Stage 3.

4.  	Stage 4.

5.  	Stage 5.

1.02  WORK INCLUDED

A.  		This Section specifies the cleaning requirements to be performed during the critical stages of construction to control contamination within the Clean Room.

B.  		The work required by this Section shall be performed by firms specializing in this occupation.

C.  		The work of this Section will commence with the beginning of Stage 3 of the Clean Room construction.

1.03  RESPONSIBILITIES

A.  		The cleaning contractor shall be responsible for:

1.  		Continuous cleanup of construction activities to meet cleanliness levels for Construction Stages 3 and 4.

2.  		Special cleanup procedures at the end of Construction Stages 3 and 4.

3.  	Full-time Cleaning Supervisor.

4.  		Portable HEPA filtered vacuum cleaners and shoe cleaners to be transferred to the SDR, and tacky matts to be replaced during construction activities.

5.  		Cleaning schedule showing tasks and locations.

B.  		The Contractor shall be responsible for a schedule that will enhance the work of the cleanup crew.

C.  		Other contractors will be required to perform the following:

1.  		Wipe down all incoming materials within the staging areas that are to be installed in the Clean Room.

2.  		Spot cleanup of respective construction areas by defined cleaning requirements.

3.  		Reclean all spot areas deemed contaminated by the Cleaning Supervisor.

1.04  RELATED SECTIONS

A.  		This Section shall be used in conjunction with the following specifications and related Contract Documents to establish the total requirements for the cleaning within the Clean Room.

1.  		All Division 1 sections included in the project specifications.

2.  		Section 13001, Clean Room Systems.

3.  		Section 15055, Clean Room Testing and Certification.

4.  		Section 15175, Clean Room Ceiling System.

5.  		Section 15833, Clean Room Recirculation Air-Handling Units.

B.  		In the event of conflicting requirements for referenced cleaning procedures between this Section and any other Section, the Provisions of this Section shall govern.

1.05  QUALITY ASSURANCE

A.  		The Contractor's personnel who perform the work required by this Section shall have a minimum of five years experience in clean room, laboratory, surgical suite, and hospital cleaning, with at least two clean room projects similar in size and scope to the referenced project.

B.  		The Cleaning Supervisor shall continuously monitor the procedures and work performed by all contractors to verify compliance with these Specifications.  Deviations shall be corrected to the satisfaction of the Cleaning Supervisor prior to further work in the affected area, or brought to the attention of the Clean Zone Director.

C.  		All cleaning personnel shall attend Stages 3 and 4 Protocol, as well as Hazardous Material Safety training classes.

D.  		All cleaning personnel shall be properly gowned for entry into the Clean Room in accordance with the posted cleanliness stage.

1.06  SUBMITTALS, SAMPLES, AND METHOD STATEMENTS

A.  		Submittals:

1.  		Provide submittal information on cleaning equipment and materials to be used for all Clean Room cleanup tasks.

2.  		Provide layout of the Clean Room showing locations of shoe brush cleaners, tacky matts, and other devices required to maintain protocol for each Cleanliness Stage.

3.  		Prepare list of cleaning crew workers and statement of qualifications.  Update list of workers at beginning of each week.

B. 	 Samples:  Provide samples of all cleaning solutions, materials, equipment, and tools proposed for the cleaning operations.

C.  	Method Statements:

1.  		Prepare method statements for cleaning procedures to be used for each Cleanliness Stage, and for each Clean Room classification.   Indicate size of cleaning crew, steps each crew will perform, sequence of work steps, cleaning procedures to be followed, preparation of solutions, and the like.

2.  		Describe frequency with which cleaning solutions are changed, wipes and sponges are replaced, and tacky matts are removed.

3.  		Describe facility utilities and services that must be operational in order to perform cleaning operations.

PART 2 - PRODUCTS

2.01  MATERIALS AND EQUIPMENT

A.  		Clean Room Filtered Vacuum Cleaners:  Individual canister dry-vacuum units affixed with four-stage filtration including 0.3 micron HEPA filter rated at 99.97 percent efficiency on the air discharge, wheeled cart, 10-foot hose, and selection of wands.  Change microfilter paper at least once a month.  Vacuums shall be Hako, Nil Fisk, or Minuteman vacuum cleaners.  Provide three new vacuum cleaners (with 2-gallon tank capacity, and one with 3-gallon tank capacity) which will become the property of the SDR at completion of the project.

B.  		Motorized Shoe Cleaners:  Packaged portable shoe cleaner with integral vacuum cleaner, 0.3 micron HEPA filter cartridge rated at 99.97 percent efficiency on the air discharge, and five scrub brushes.  Change microstatic filter cartridge as described in Part 3 of this Section.  Cleaners shall be similar to Model D-2000-VA by Clean Room Products, or Model 100-FJ by Liberty.  Provide three new shoe cleaners which will become the property of the SDR at completion of the project.

C.  		Tacky Rags:  Lint-free, particulate-free, sticky surface rags, Tex-Wipes by the Texwipe Company.

D.  		Lint-Free Towels:  Lint-free, particulate-free wipes rated for clean room use, Tex Clean 100 by the Texwipe Company.

E.  		Wipes:  Nylon tricot 1068 or similar material suitable for clean room duty, Laminaire or Miracle Wipe.

F.  		Tacky Matts:  Removable sticky matts of 2-mil polyethylene, 120-pack, similar to Clean Line Sticky Matts by Control Environment Corp., or Type D 1100 by Clean Room Products.

G.  		Masslinn wipe towels, sweep tool, and mop handles by National Sanitary Supply.

H.  		Mops and Sponges:  Cellulose material by A.J. Reynolds Co.

I.  		Hydrowash Equipment:  A 200 psi water jet nozzle hose and pump system providing a constant flow of 60 gpm using potable water.

J.  		Water:  Deionized water.

K.  		Waste Water Pumps:  Pumps and hose as required to evacuate waste water during the hydrowash procedures.

L.  		Black and White Felt:  24 inches square, 10 inches square when folded, black and white, static-free natural fiber felt folded with cut edges inside.

M. 		Buckets:  Stainless steel in Clean Room.  No substitutes will be accepted.  One will be labeled for floor mopping, the other for wiping equipment.  All buckets shall be thoroughly cleaned and dried after each use.

N.  		Ladders:  Aluminum or fiberglass.

2.02  CLEANING SOLUTIONS

A.  		Cleaning Solution:  A mixture of deionized water, filtered with 10-minute circulation through DI mixed bed and 0.2 micron final filters, then mixed with a 10 percent dilution of staticide surfactant cleaning solution.

B.  		Solvents:  Filtered to 0.2 microns.  An aziotropic mixture formulated with a low residue level for use in clean rooms.  The solvent shall be suitable for clean hard surfaces including plastic, PVC, and laminated surfaces, similar to Lab-Clean EKC by Tech Distributors, Inc.  Only reagent and transistor grade solvents shall be used.  When possible, denatured alcohol shall be used because of its lower toxicity level.

C.  		Bactericidal Solution:  Filtered to 0.2 microns.  A solution formulated for use in clean rooms.  The product shall be noncorrosive, low toxicity using a bactericidal liquid in deionized water.

D.  		Low-Residue Antistatic Detergent:  A low-foam antistatic neutral detergent that contains less than 1 ppm sodium and potassium.

E.  		Soap Wash:  Nonionic, nonphosphate liquid detergent; Ivory Liquid by Proctor and Gamble.

F.  		Wax or Soap Granules:  Not permitted in the Clean Room.

PART 3 - EXECUTION

3.01  CLEANING PROCEDURES

A.  		Stage 1:

1.  		Continuous Cleaning Procedures During Stage 1:  Performed by contractors in accordance with Section 13001, Clean Room Systems.

2.  		Special Clean Procedures at Completion of Stage 1:  Performed by contractors in accordance with Section 13001, Clean Room Systems.

B.  		Stage 2:

1.  		Continuous Cleaning Procedures During Stage 2:  Performed by contractors in accordance with Section 13001, Clean Room Systems.

2.  		Special Cleaning Procedures at Completion of Stage 2:  Performed by contractors in accordance with Section 13001, Clean Room Systems.

C.  		Stage 3:

1.  		Continuous Cleaning Procedures During Stage 3:

a.  	Remove trash and debris, sweep, and vacuum all surfaces continuously.

b.  	Remove trash by removing the polyethylene liners with the trash contained.  Do not transfer trash from one container to another.  Insert new polyethylene liners inside trash containers and secure by turning the top of the bag over the lip of the container.

c.  	Wipe down ceiling components, wall panels and studs, ducting, plenums, VLF ceiling modules, and equipment being introduced into the Clean Room with wipes moistened with cleaning solution.

d.  	Clean all construction and cleaning tools and equipment used inside the Clean Room with wipes moistened with cleaning solution prior to entry into the Clean Room.

e.  	Vacuum all floor surfaces in the Clean Room at the end of every workday with clean room filtered vacuum cleaners, or with the built-in house vacuum system.

f.  		Replace tacky matts daily, and shoe cleaner filter cartridges every two weeks or as necessary.

g.  	Wipe down all concealed wall studs, floor stanchions, and concealed cavities immediately before the finish wall and floor panels are installed so that no foreign material remains sealed inside hidden recesses.

h.  	Wipe down all vertical wall surfaces installed inside the Clean Room at the end of each week with wipes moistened with clean room cleaning solution.

i.  		Vacuum and wet mop the Personnel Gowning Area and Equipment Staging Area during each break and at the end of each construction shift so that the areas are always clean when the work crews return to the Clean Room.

2.  		Special Cleaning Procedures at Completion of Stage 3:

a. 		Vacuum all surfaces in the Clean Room with clean room filtered vacuum cleaners, or with the built-in house vacuum system, using special wands as required to protect finishes of all materials and equipment.

b.  	Remove all protective wraps and coatings from wall panels, floor, ceiling components, ducts, and plenums to expose final finish.  Take care to protect all finished surfaces during each cleaning operation.

c.  	Prepare special cleaning solution using deionized water and staticide surfactant cleaning solution.

d.  	Wipe down all interior and exterior surfaces of air ducts and plenums, access walkways, structure, utility piping, electric raceways, support stanchions and hangers, pass-throughs, ceiling grid runners, interior and exterior surfaces of the lights, and any special appurtenances anywhere within the Clean Room.  Use damp wipes moistened with clean room cleaning solution.

e.  	Clean all finished wall surfaces and exposed structure using an organized wipedown procedure with block sponges moistened in clean room cleaning solution.  Wipe each section of wall with three passes in one direction, rinse the sponge, and wipe again with three passes in a direction 90 degrees opposed to the first pass.

f.  		Using a foam strip sponge and clean room cleaning solution, wet mop the floor in overlapping sections.  Change the water often.  Perform mopping from the cleanest end toward the dirtiest end of each area.

g.  	Vacuum the floor after all other surface cleaning activities are completed.

h.  	Vacuum with clean room filtered vacuum cleaner, then wipe down the inside surfaces of all clean room makeup and recirculation air handlers with wipes moistened with clean room cleaning solution.

i.  		Discard sponges and cleaning solution.

D.  		Stage 4:

1. 	 Continuous Cleaning Procedures During Stage 4:

a. 		Monitor cleanup of process equipment at the staging area to ensure the outer clean wrap is removed and the equipment cleaned by the SDR.

b.  	Protect all finished surfaces during each cleaning operation.

c.  	Vacuum all floor surfaces in the Clean Room at the end of every workday with clean room filtered vacuum cleaners, or with the built-in house vacuum system.

d.  	Replace tacky matts weekly, and shoe cleaner filter cartridges every month or as required.

e.  	Clean all cleaning tools and equipment used inside the Clean Room with wipes moistened with cleaning solution prior to entry into the Clean Room.

f. 		Clean all external and internal surfaces of ceiling plenum module, filter grid, walls, light fixtures, etc. with wipes moistened with clean room cleaning solution.  Wipe each section in three passes in one direction, then three passes in a direction 90 degrees opposed to the first pass.

g.  	At this point, request operation of the air handling system and permit the recirculation fan systems to operate continuously for 24 hours in order to flush the system with air.

h.  	Following the 24-hour fan purge period, all internal surfaces of the ceiling assembly shall be cleaned again with wipes moistened with clean room cleaning solution.  Wipe down inside and outside of filter grid, and other ceiling appurtenances.

i.  		At this point, the continuous foam gasket or ceiling liquid gel filter sealant can be prepared and placed in the ceiling filter grid trough by the manufacturer.  Full cure time shall be reserved before proceeding with cleaning procedures.

j.  		Clean all finished wall surfaces and exposed structure using an organized wipedown procedure solution.  Wipe each section of wall with three passes in one direction, rinse the sponge, and wipe again with three passes in a direction 90 degrees opposed to the first pass.

k.  	Using a foam strip sponge and clean room cleaning solution, wet mop the floor in overlapping sections that do not exceed 25 square feet between rinses of the mop.  Change the water often.  Perform mopping from the cleanest end toward the dirtiest end of each area.

l.  		Perform random black and white felt rubdown tests on all surfaces.  Use only one side of cloth.

m.  Vacuum the floor after all other surface cleaning activities are completed.  Replace the felt pads on the vacuum head whenever necessary to prevent scratching and scraping of the floor surface.

n.  	Never open the vacuum cleaner in the Clean Room to changer filter, bags, or to perform other maintenance.

o.  	Monitor the contractor responsible for the ceiling installation to ensure outer wrap is removed from ULPA filter cartons and the inner packing box is wiped down prior to entry into clean room.

p.  	Perform black and white felt rubdown test on each ULPA filter module as it is unpacked by the ceiling contractor and installed in the ceiling grid.  Notify Clean Room Director when filter modules do not comply with Clean Room standards specified.

q.  	At this point, ULPA filter modules can be installed in the ceiling grid.

2.  		Special Cleaning Procedures at Completion of Stage 4:

a.  	At this point, request operation of the recirculation fans with ULPA ceiling filters in place in order to flush the system with clean air.  Allow room conditions to stabilize for a minimum of 24 hours prior to entering the Clean Room.

b.  	Following the 24-hour fan purge period, clean all internal surfaces of the Clean Room again using wipes moistened with clean room cleaning solution.  This includes the rated areas of clean room service aisles, as well as all spaces used for air migration such as underfloor plenum, subfab, air shafts, interstitial, and fan deck.

c.  	Protect all finished surfaces during each cleaning operation.

d.  	Clean the outside of all light fixtures, the edges of the filter grid, and other ceiling components.  Take care not to touch any filter media.

e.  	Clean all finished wall surfaces and exposed structure using an organized wipedown procedure with block sponges moistened in clean room cleaning solution.  Wipe each section of wall with three passes in one direction, rinse the sponge, and wipe again with three passes in a direction 90 degrees opposed to the first pass.

f.  		Using a foam strip sponge and clean room cleaning solution, wet mop the floor in overlapping sections that do not exceed 25 square feet between rinses of the mop.  Change the water often.  Perform mopping from the cleanest end toward the dirtiest end of each area.

g.  	Vacuum the floor after all other surface cleaning activities are completed.

h.  	Secure the area so that no traffic occurs in cleaned are for a 4-hour drying period.

E.  		Stage 5:

1.  		Continuous Cleaning Procedures During Stage 5:  Cleaning will be performed by SDR.

2.  		Special Cleaning Procedures at Completion of Stage 5:  Cleaning will be performed by SDR.

END OF SECTION